| Your Company Name / Logo | INSTRUMENT AIR QUALITY TEST SOP | Doc no: SOP INST 018 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To protect positioners, I/P converters and actuators from water, oil and dirt in the air supply.

# 2. Scope

Instrument air systems from dryer outlet to the farthest users.

# 3. References

- ANSI/ISA 7.0.01 quality standard for instrument air

- ISO 8573-1 air purity classes

- Dryer and filter manuals

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Bleed air slowly; compressed air jets can injure.

# 6. Tools and equipment

- Portable dew point meter

- Oil and particle test kit or filter membrane holder

- Pressure gauge

# 7. Prerequisites

- Test points identified: dryer outlet and end of headers.

# 8. Procedure

## 8.1 Dew point

- Connect the dew point meter at line pressure and wait for a stable reading.

- Compare with the requirement: at least 10 °C below the minimum ambient temperature (ISA 7.0.01).

## 8.2 Oil and particles

- Pass a measured volume of air through the test membrane or detector tube.

- Compare with the site limit or ISO 8573-1 class.

## 8.3 Pressure

- Record header pressure at the end user during normal demand.

## 8.4 Record and act

- Record results; raise work orders for dryer, filter or drain problems.

# 9. Acceptance criteria

- Pressure dew point at least 10 °C below minimum ambient.

- Oil and particles within site limits.

- Supply pressure within the design range at end users.

# 10. Records

- Instrument air header schedule (free template: instrumentationblog.in/downloads/templates/instrument-air-header-schedule/)

- Instrument maintenance log (free template: instrumentationblog.in/downloads/templates/instrument-maintenance-log/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.