| Your Company Name / Logo | INSTRUMENT ISOLATION AND LOTO SOP | Doc no: SOP SAF 001 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To protect people and the process when field instruments are removed or worked on.

# 2. Scope

Field instruments connected to process lines or vessels, and their electrical and pneumatic supplies. It supplements, and does not replace, the site permit and isolation procedure.

# 3. References

- Site permit to work and isolation procedure

- P&IDs and hook up drawings

- Safety data sheets for the process fluid

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- For hazardous, toxic or high pressure services use double block and bleed isolation where required by the site procedure.

- Never rely on a control valve as an isolation valve.

# 6. Tools and equipment

- Personal locks, tags and lockout devices

- Drain container and spill kit

- Gas detector where applicable

- Correct tools and PPE for the fluid

# 7. Prerequisites

- Permit issued; isolation points identified on the P&ID and hook up drawing.

- Affected control loops in manual and any trips bypassed under authorisation.

# 8. Procedure

## 8.1 Process isolation

- Close the instrument root valve(s) or manifold block valves.

- Open vent and drain valves slowly to depressurise and drain into a container.

- Verify zero pressure on a gauge or by observing that venting has stopped.

## 8.2 Electrical and pneumatic isolation

- Isolate the loop power at the marshalling or by the field breaker where required (most 4 to 20 mA loops can be worked on live only if the site rules allow).

- Isolate instrument air at the filter regulator and vent the actuator for valves.

## 8.3 Lock and tag

- Apply personal locks and tags to every isolation point listed on the permit.

- Try to operate (test) where safe, to confirm the isolation is effective.

## 8.4 Return to service

- Reinstall and leak test the instrument.

- Remove locks and tags only after the work is complete and the area is clear.

- De isolate in reverse order with operations, then remove bypasses and close the permit.

# 9. Acceptance criteria

- Zero energy verified before work starts.

- All locks and tags removed and isolation reversed after work.

- No leaks on return to service.

# 10. Records

- Permit to work and isolation certificate (site forms) (free template: instrumentationblog.in/downloads/templates/)

- Instrument breakdown report (free template: instrumentationblog.in/downloads/templates/instrument-breakdown-report/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.