| Your Company Name / Logo | LEVEL SWITCH FUNCTIONAL TEST SOP | Doc no: SOP INST 010 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To prove that level switches detect the liquid at the right point and that the alarm or trip they initiate works.

# 2. Scope

Vibrating fork, float and displacer type point level switches in alarm, interlock and safety service.

# 3. References

- Switch manufacturer manual (test function)

- Alarm and trip list, cause and effect matrix

- Proof test procedure for SIS switches

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- If the switch is part of a SIS trip, use the approved bypass and proof test procedure.

- Removing a switch from a vessel may need the vessel drained and isolated: never open a nozzle under pressure.

# 6. Tools and equipment

- Multimeter

- Manufacturer test magnet or test button tool (for switches with a test function)

- Bucket of process compatible liquid for removed switches

- Radio for communication with the control room

# 7. Prerequisites

- Permit approved; operations informed which alarms and trips will be activated.

- Bypass in place where required for trips.

- Switch set point and action (open or close on high level) known from the alarm and trip list.

# 8. Procedure

## 8.1 Choose the test method

- Best: raise or lower the real level to the switch point under controlled conditions (proves switch and installation).

- Next: use the built in or magnetic test function, which simulates the switch state (proves electronics and wiring, not the process contact).

- Otherwise: remove the switch and immerse it in liquid (proves the sensor, but needs isolation and drain).

## 8.2 Test the switch

- Perform the test using the chosen method and observe the switch status LED or output.

- Check that the switch changes state at the expected condition and returns when the condition clears.

- For fork switches, check the time delay setting if fitted.

## 8.3 Check the alarm and trip path

- Confirm with the control room that the correct alarm appears with the correct tag and priority.

- For trip switches, confirm the logic solver output and, where the procedure allows, the final element action.

- Check that the switch fails to the safe state on loss of power (disconnect the supply briefly if the procedure allows).

## 8.4 Restore

- Reset alarms, remove bypasses and confirm the switch shows the normal state for the current level.

- Close the permit and record the test.

# 9. Acceptance criteria

- Switch changes state at the required level (or test condition) and resets correctly.

- Correct alarm or trip received in the control system.

- Switch goes to the safe state on loss of power where designed fail safe.

# 10. Records

- SIL proof test record (for SIS switches) (free template: instrumentationblog.in/downloads/templates/sil-proof-test-record/)

- Alarm and trip list (free template: instrumentationblog.in/downloads/templates/alarm-and-trip-list/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.