| Your Company Name / Logo | DP LEVEL TRANSMITTER CALIBRATION SOP | Doc no: SOP INST 011 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To make sure DP level transmitters read the true level over their range, including the effect of wet legs, seals and mounting height.

# 2. Scope

DP and pressure transmitters used for level on open and closed vessels, with dry legs, wet legs or remote seals.

# 3. References

- Level transmitter data sheet and range calculation

- Manufacturer manual

- Vessel drawing with tap elevations

- Site calibration procedure for pressure transmitters

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Close and drain impulse lines slowly; hot or toxic liquid may be trapped in legs and seal pots.

- Do not open remote seal capillaries; they are sealed systems.

# 6. Tools and equipment

- Pressure calibrator with low range module, or pressure and vacuum source

- HART communicator

- Range calculation sheet with LRV and URV in mbar

- Fill liquid for wet legs if required

# 7. Prerequisites

- Range calculation checked: process SG, tap spacing, wet leg or seal head.

- Operations agree on the level loop being out of service; alarms and trips inhibited as authorised.

# 8. Procedure

## 8.1 Prepare

- Isolate the transmitter with the manifold and vent both sides safely.

- Record the configured LRV, URV, damping and output mode.

## 8.2 As found test

- Apply pressure to the HP side (or vacuum to LP for negative values) at 0, 25, 50, 75 and 100 % of span, rising and falling.

- Record the output at each point on the calibration report.

## 8.3 Adjust

- If any point fails, trim zero and span (sensor trim) with the communicator.

- Repeat the 5 point test and record as left values.

## 8.4 Wet leg and seal check

- Refill the wet leg to its seal pot level with the specified liquid and vent gas.

- For seals, confirm the transmitter height and capillary route match the range calculation.

## 8.5 Return to service and verify

- Open the manifold in the correct order, close the equaliser last.

- Compare the transmitter level with a gauge glass or manual dip; investigate a difference.

- Remove inhibits and inform the control room.

# 9. Acceptance criteria

- As left error within tolerance at all points (for example ± 0.25 % of span).

- Level reading agrees with the local gauge within the agreed limit.

- Wet legs full, seals intact, records complete.

# 10. Records

- Level transmitter calibration report (free template: instrumentationblog.in/downloads/templates/level-transmitter-calibration-report/)

- Calibration master list (free template: instrumentationblog.in/downloads/templates/calibration-master-list/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.