| Your Company Name / Logo | PH ANALYSER CALIBRATION SOP | Doc no: SOP ANA 001 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To keep online pH measurements accurate by calibrating the electrode and transmitter against standard buffers.

# 2. Scope

Online pH analysers with glass electrodes and automatic temperature compensation.

# 3. References

- Analyser and electrode manuals

- Buffer solution certificates

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Process liquid may be corrosive: wear chemical gloves and goggles.

- Handle glass electrodes carefully; they break easily.

# 6. Tools and equipment

- Fresh pH buffers (pH 7.00 and pH 4.01, or pH 10.01 for alkaline processes) within expiry

- Clean beakers and deionised water

- Soft tissue (do not rub the glass bulb)

# 7. Prerequisites

- Loop in manual or alarms inhibited; electrode accessible via retractable holder or bypass.

# 8. Procedure

## 8.1 Cleaning

- Remove the electrode, rinse with deionised water and clean any coating as recommended by the manufacturer.

## 8.2 Two point calibration

- Start the calibration routine on the transmitter.

- Immerse in pH 7 buffer, wait for a stable reading and accept.

- Rinse, immerse in pH 4 (or pH 10) buffer, wait for stability and accept.

- Record the slope (%) and offset (zero point, mV) shown by the transmitter.

## 8.3 Completion

- Rinse and reinstall the electrode; check the process reading is reasonable.

- Release the loop to automatic.

# 9. Acceptance criteria

- Slope typically 95 to 102 % of the theoretical value (replace the electrode if below the manufacturer limit, often about 85 to 90 %).

- Offset (zero point) typically within ± 30 mV.

- Stable reading in both buffers.

# 10. Records

- Calibration master list (free template: instrumentationblog.in/downloads/templates/calibration-master-list/)

- Instrument PM schedule (free template: instrumentationblog.in/downloads/templates/instrument-preventive-maintenance-schedule/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.