| Your Company Name / Logo | PRESSURE SWITCH CALIBRATION SOP | Doc no: SOP INST 006 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To verify that pressure switches operate at the specified set point with acceptable repeatability and deadband.

# 2. Scope

Mechanical and electronic pressure switches used for alarms, interlocks and trips.

# 3. References

- Alarm and trip set point list

- Switch manufacturer manual

- SIS proof test procedure where the switch is part of a SIF

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- A switch in a trip circuit must be bypassed under the approved bypass procedure before testing, and the bypass removed afterwards.

# 6. Tools and equipment

- Pressure source with reference gauge or calibrator

- Continuity tester or multimeter

- Tools for set point adjustment

# 7. Prerequisites

- Set point, direction (rising or falling) and tolerance taken from the controlled alarm and trip list.

# 8. Procedure

## 8.1 Test

- Isolate and vent the switch, connect the pressure source.

- Connect the continuity tester across the contact used in the circuit (NO or NC).

- Increase pressure slowly near the set point; record the pressure at which the contact changes (trip).

- Decrease pressure until the contact returns; record the reset value.

- Repeat for three trials.

## 8.2 Adjustment

- If the trip value is out of tolerance, adjust the range screw, lock it, and repeat three trials.

- Check the deadband; adjust if the switch has an adjustable differential.

## 8.3 Functional check

- Reconnect and, with the bypass still in place, trip the switch and confirm the alarm or trip status in the control system.

- Return the switch to service and remove the bypass with operations approval.

# 9. Acceptance criteria

- Trip within the set point tolerance on every trial.

- Repeatability within the specified limit; deadband acceptable for the application.

- Correct alarm or trip indication in the control system.

# 10. Records

- Pressure switch calibration report (free template: instrumentationblog.in/downloads/templates/pressure-switch-calibration-report/)

- Alarm and trip set point list (free template: instrumentationblog.in/downloads/templates/alarm-and-trip-list/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.