| Your Company Name / Logo | PRESSURE TRANSMITTER CALIBRATION SOP | Doc no: SOP INST 001 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To verify and, where necessary, adjust the accuracy of pressure transmitters so that their output stays within the specified tolerance.

# 2. Scope

Gauge and absolute pressure transmitters with 4 to 20 mA output, with or without HART, calibrated in the field or in the instrument workshop.

# 3. References

- Manufacturer instruction manual of the transmitter

- Instrument data sheet and loop drawing

- Site calibration and isolation procedures

- ISO 9001 clause 7.1.5 (monitoring and measuring resources)

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Isolate, depressurise and vent the transmitter before disconnecting; toxic or hot process fluids need draining to a safe place.

- Never exceed the transmitter overpressure limit when applying test pressure.

# 6. Tools and equipment

- Pressure calibrator or hand pump with reference gauge, at least 4 times more accurate than the transmitter

- mA meter or documenting process calibrator (loop power if required)

- HART communicator or configuration software

- 250 Ω resistor for HART communication on the bench

- Test hoses and fittings rated for the test pressure

- Calibration report form

# 7. Prerequisites

- Permit approved and the loop put in manual or bypassed by operations.

- Reference standard within its calibration validity.

- Data sheet values available: LRV, URV, unit, tolerance.

# 8. Procedure

## 8.1 Isolation

- Ask operations to put the control loop in manual or bypass any trip using the approved bypass procedure.

- Close the root or manifold block valve, open the vent or drain valve and confirm that the pressure is zero.

- Connect the pressure source to the test port or manifold, and the mA meter in series with the loop (or use the test terminals).

## 8.2 As found test

- Record the transmitter configuration (range, damping, units) with the HART communicator.

- Apply pressure at 0, 25, 50, 75 and 100 % of span, approaching each point from below, and record the output in mA.

- Continue downscale at 75, 50, 25 and 0 %, approaching each point from above.

- Calculate the error in % of span at each point. If all errors are within tolerance, no adjustment is needed.

## 8.3 Adjustment

- If any point is out of tolerance, perform a sensor trim (lower and upper) with the HART communicator using the reference pressures.

- If the mA output itself is wrong, perform a 4 mA and 20 mA output (D/A) trim against the mA meter.

- Do not change the range unless authorised; ranging is a configuration change, not a calibration.

## 8.4 As left test

- Repeat the 5 point upscale and downscale test and record the as left readings.

- Confirm that all points are within tolerance.

## 8.5 Return to service

- Remove the test equipment, close the vent and drain valves and reinstate the plugs.

- Open the block valve slowly and check for leaks.

- Confirm with the control room that the reading is correct and normal for the process, then hand back the loop and close the permit.

# 9. Acceptance criteria

- As left error at every point within the specified tolerance (typically ± 0.25 % of span unless stated otherwise).

- No leaks at the process connections after return to service.

- Reading in the DCS matches the expected process value.

# 10. Records

- Pressure transmitter calibration report (free template: instrumentationblog.in/downloads/templates/pressure-transmitter-calibration-report/)

- Calibration master list (update the next due date) (free template: instrumentationblog.in/downloads/templates/calibration-master-list/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.