| Your Company Name / Logo | RADAR LEVEL TRANSMITTER COMMISSIONING SOP | Doc no: SOP COM 004 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To configure and prove radar level transmitters so they measure the true level over the full range.

# 2. Scope

Non contact (free space) and guided wave radar level transmitters on tanks and vessels.

# 3. References

- Transmitter manual and configuration software

- Tank drawing (height, nozzle, internals)

- Instrument data sheet

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- Tank roof work needs fall protection and, for some fluids, gas testing.

# 6. Tools and equipment

- Configuration tool (HART, display or software) able to show the echo curve

- Dip tape or reference level gauge

- mA meter

# 7. Prerequisites

- Transmitter installed according to the manual (nozzle size and length, distance from wall and inlet).

# 8. Procedure

## 8.1 Basic configuration

- Enter the tank height (reference point to tank bottom), the empty and full calibration distances, and the measuring units.

- Set the blocking (near zone) distance and the medium properties (dielectric constant range, surface conditions).

## 8.2 False echo suppression

- With the tank as empty as practical, record a false echo map so that echoes from internals and nozzles are ignored.

- Check the echo curve: the level echo must be clearly above the threshold.

## 8.3 Output and verification

- Set damping (typically a few seconds) and the failure current (NAMUR NE 43).

- Compare the reading with a manual dip at two or more levels.

- Check the mA output and DCS reading.

# 9. Acceptance criteria

- Reading agrees with the manual dip within the specified tolerance.

- Clear, stable level echo over the operating range.

- Correct output and alarms in the DCS.

# 10. Records

- HART configuration record (free template: instrumentationblog.in/downloads/templates/hart-transmitter-configuration-record/)

- Loop check sheet (free template: instrumentationblog.in/downloads/templates/loop-check-sheet/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.