| Your Company Name / Logo | SAFETY SYSTEM BYPASS AND OVERRIDE PROCEDURE | Doc no: SOP SIS 001 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To make sure no safety function is left disabled without control, approval and compensating protection.

# 2. Scope

Bypasses of SIS functions, BPCS interlocks, fire and gas inputs and safety critical alarms.

# 3. References

- IEC 61511 operation and maintenance requirements

- Safety requirements specification

- Site permit and MOC procedures

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- A bypassed safety function leaves the hazard unprotected: apply compensating measures before bypassing.

- Only authorised persons may apply or remove bypasses.

- Bypasses must be visible to operators at all times.

# 6. Tools and equipment

- Bypass register

- Bypass request form or permit

- Cause and effect matrix

# 7. Prerequisites

- Reason for bypass defined (maintenance, testing, start up).

- Hazard and compensating measures assessed.

# 8. Procedure

## 8.1 Request and assess

- Identify the function, hazard and reason.

- Define compensating measures such as an operator watching a redundant reading.

- Set the planned removal time.

## 8.2 Approve

- Obtain approval at the level required (higher for SIS functions).

- Enter the bypass in the register.

## 8.3 Apply

- Apply the bypass with the control room; confirm it is indicated on the operator screen.

- Put compensating measures in place.

## 8.4 Monitor

- Review active bypasses every shift; overdue bypasses escalate.

- Long term bypasses go through management of change.

## 8.5 Remove

- Remove the bypass, confirm the function is healthy, and close the register entry.

# 9. Acceptance criteria

- Every bypass approved, registered, visible and time limited.

- Compensating measures in place while active.

- Bypasses removed and recorded promptly.

# 10. Records

- Bypass and override register (free template: instrumentationblog.in/downloads/templates/bypass-override-register/)

- MOC form (free template: instrumentationblog.in/downloads/templates/moc-form-template/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.