| Your Company Name / Logo | CONTROL VALVE POSITIONER CALIBRATION SOP | Doc no: SOP INST 012 | Rev: 0 |
| --- | --- | --- | --- |
| Department: Instrumentation | Standard operating procedure | Date: | Page: see footer |

# 1. Purpose

To make the valve position follow the control signal accurately and smoothly over its full travel.

# 2. Scope

Digital (HART or fieldbus) and pneumatic positioners on linear and rotary control valves.

# 3. References

- Positioner and valve manuals

- Control valve data sheet (fail action, travel, characteristic)

- Loop diagram

# 4. Responsibilities

- Instrument technician: carries out the work and records results.

- Instrument engineer or supervisor: reviews and approves the records.

- Operations: grants the permit, isolates the process and returns the equipment to service.

# 5. Safety precautions

- Work only under a valid permit to work and follow the site isolation (lockout tagout) procedure.

- Wear the PPE required for the area: safety helmet, glasses, gloves and safety shoes as a minimum.

- In hazardous areas use certified or intrinsically safe test equipment, or obtain a gas free certificate and hot work permit.

- Inform the control room before starting, and before returning the instrument to service.

- The valve will move during calibration: agree with operations, and isolate or bypass the process if needed.

- Keep hands clear of the yoke, stem and linkage while air is applied.

# 6. Tools and equipment

- mA source or calibrator

- HART communicator or configuration software

- Supply pressure gauge

- Tools to adjust linkage and feedback arm

# 7. Prerequisites

- Valve isolated or loop in manual with operations approval.

- Air supply clean, dry and at the specified pressure.

# 8. Procedure

## 8.1 Mechanical checks

- Check feedback arm or magnet is tight and correctly positioned at 50 % travel.

- Check the actuator for leaks and the stem for damage; correct packing tightness.

## 8.2 Calibrate

- Run the positioner autocalibration (travel calibration) as described in the manual.

- For manual types, set zero at 4 mA and span at 20 mA and repeat until both hold.

## 8.3 5 point stroke test

- Apply 4, 8, 12, 16 and 20 mA rising and falling.

- Record actual travel from the scale or feedback and the time to settle.

- Check fail action by removing air or signal as allowed.

## 8.4 Tune and finish

- Use autotune or adjust gain to give a fast response without overshoot.

- Save a valve signature if the positioner supports it.

- Return the loop to automatic with operations.

# 9. Acceptance criteria

- Travel error within tolerance at each point (for example ± 1 % of travel).

- No hunting or overshoot; correct fail action.

- Records and signature saved.

# 10. Records

- Control valve calibration report (free template: instrumentationblog.in/downloads/templates/control-valve-calibration-report/)

- HART configuration record (free template: instrumentationblog.in/downloads/templates/hart-transmitter-configuration-record/)

# 11. Approval

|  | Prepared by | Reviewed by | Approved by |
| --- | --- | --- | --- |
| Name |  |  |  |
| Signature |  |  |  |
| Date |  |  |  |

This procedure is a generic template. Adapt it to your site permit system, the manufacturer instructions and your quality system before use.