## How to Use
HOW TO USE: 24 V DC POWER SUPPLY LOAD LIST
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. List every load with quantity and current.
2. Use worst case current, not typical.
3. Set the design margin.
4. Read the required supply rating.
5. Select supplies and redundancy, and size fuses per circuit.
What the formulas do
• Total (mA) = quantity × current each.
• Power (W) = total (mA) × V ÷ 1000.
• Required rating = total current × (1 + margin).
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
24 V DC POWER SUPPLY LOAD LIST
Company: Your Company Name / Logo |  |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Power supply data
Panel / cabinet |  |  |  |  | Nominal voltage (V)
Design margin (%) |  |  |  |  | Redundancy
Loads
No | Tag / item | Description | Qty | Current each (mA) | Total (mA) | Power (W) | Fuse / MCB | Continuous? | Remarks
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
Total current (A) | [7 empty] | 0
Total power (W) | [7 empty] | 0
Required rating with margin (A) | [7 empty] | 0
Use worst case currents: 22 mA for 4 to 20 mA loops, inrush for solenoids and relays. Choose the next standard power supply size above the required rating.
Prepared by |  |  |  |  | Checked by
Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date:

## Example
24 V DC POWER SUPPLY LOAD LIST
Company: ABC Process Industries Ltd |  |  |  |  | Doc no: PSU LL 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Power supply data
Panel / cabinet |  | PLC panel CP 01 |  |  | Nominal voltage (V) |  | 24
Design margin (%) |  | 25 |  |  | Redundancy |  | N+1, two 20 A modules
Loads
No | Tag / item | Description | Qty | Current each (mA) | Total (mA) | Power (W) | Fuse / MCB | Continuous? | Remarks
1 | PLC CPU | CPU and backplane | 1 | 800 | 800 | 19.2 | 2 A | Yes
2 | AI cards | Loop powered transmitters at 22 mA | 32 | 22 | 704 | 16.896 | 4 A | Yes
3 | DO cards | Interposing relays | 24 | 25 | 600 | 14.4 | 2 A | Yes
4 | Solenoids | Valve solenoids 2 W | 8 | 85 | 680 | 16.32 | 2 A | Yes
5 | Switch | Ethernet switch | 1 | 400 | 400 | 9.6 | 1 A | Yes
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
Total current (A) | [7 empty] | 3.184
Total power (W) | [7 empty] | 76.416
Required rating with margin (A) | [7 empty] | 3.98
Use worst case currents: 22 mA for 4 to 20 mA loops, inrush for solenoids and relays. Choose the next standard power supply size above the required rating.
Prepared by |  |  |  |  | Checked by
Name: |  |  |  |  | Name:
Signature: |  |  |  |  | Signature:
Date: |  |  |  |  | Date: