## How to Use
HOW TO USE: CABLE CONTINUITY AND LOOP RESISTANCE TEST RECORD
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter length and conductor size for each pair from the cable schedule.
2. Short the pair at the far end.
3. Measure loop resistance at the near end.
4. Compare with the expected value; high readings point to loose or wrong terminations.
5. Remove shorts and restore terminations.
What the formulas do
• Expected loop resistance = 2 × length × 0.0172 ÷ cross section (Ω).
• PASS if measured ≤ expected × (1 + allowed excess).
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
CABLE CONTINUITY AND LOOP RESISTANCE TEST RECORD
Company: Your Company Name / Logo | [5 empty] | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Test details
Area / system | [5 empty] | Meter and cert. no
Allowed excess over expected (%) | [5 empty] | Date
Continuity results
No | Cable tag | Pair | From | To | Length (m) | Size (mm²) | Expected loop (Ω) | Measured loop (Ω) | Result | By | Remarks
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
Pairs tested | [9 empty] | 0
Pairs failed | [9 empty] | 0
Expected value uses copper resistivity 0.0172 Ω·mm²/m at 20 °C. Short the pair at the far end, measure at the near end, and remove the short afterwards.
Tested by | [5 empty] | Witnessed by
Name: | [5 empty] | Name:
Signature: | [5 empty] | Signature:
Date: | [5 empty] | Date:

## Example
CABLE CONTINUITY AND LOOP RESISTANCE TEST RECORD
Company: ABC Process Industries Ltd | [5 empty] | Doc no: CONT TEST 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Test details
Area / system |  |  | Area 200 |  |  | Meter and cert. no |  |  | Multimeter, CC 24802
Allowed excess over expected (%) |  |  | 20 |  |  | Date |  |  | 2026-10-25
Continuity results
No | Cable tag | Pair | From | To | Length (m) | Size (mm²) | Expected loop (Ω) | Measured loop (Ω) | Result | By | Remarks
1 | MC 2001 | 1 | JB 2001 | MAR 01 | 250 | 1 | 8.6 | 8.9 | PASS | Tech B
2 | MC 2001 | 2 | JB 2001 | MAR 01 | 250 | 1 | 8.6 | 8.8 | PASS | Tech B
3 | MC 2001 | 3 | JB 2001 | MAR 01 | 250 | 1 | 8.6 | 15.2 | FAIL | Tech B | Loose terminal at JB
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
Pairs tested | [9 empty] | 3
Pairs failed | [9 empty] | 1
Expected value uses copper resistivity 0.0172 Ω·mm²/m at 20 °C. Short the pair at the far end, measure at the near end, and remove the short afterwards.
Tested by | [5 empty] | Witnessed by
Name: | [5 empty] | Name:
Signature: | [5 empty] | Signature:
Date: | [5 empty] | Date: