## How to Use
HOW TO USE: INSTRUMENT CABLE INSULATION RESISTANCE TEST RECORD
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the test instrument and minimum acceptable IR from the specification.
2. Disconnect both ends and isolate electronics.
3. Test core to core, core to earth and core to screen at the specified voltage.
4. Record the lowest reading for each test.
5. Investigate and retest any failed cable.
What the formulas do
• Result = PASS if the lowest of the three readings ≥ minimum IR.
• Totals at the bottom.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
INSTRUMENT CABLE INSULATION RESISTANCE TEST RECORD
Company: Your Company Name / Logo | [5 empty] | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Test details
Area / system | [5 empty] | Insulation tester and cert. no
Minimum acceptable IR (MΩ) | [5 empty] | Date
Insulation resistance results
No | Cable tag | From | To | Cores | Test voltage (V) | Core to core (MΩ) | Core to earth (MΩ) | Core to screen (MΩ) | Result | By | Remarks
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
Cables tested | [9 empty] | 0
Cables failed | [9 empty] | 0
Disconnect cables from instruments and system cards before testing: test voltage can damage electronics. Discharge cores after testing. Use the minimum IR from your project specification.
Tested by |  |  |  | Witnessed by |  |  |  | Approved by
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date:

## Example
INSTRUMENT CABLE INSULATION RESISTANCE TEST RECORD
Company: ABC Process Industries Ltd | [5 empty] | Doc no: IR TEST 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Test details
Area / system |  |  | Area 200, SYS 300 |  |  | Insulation tester and cert. no |  |  | IR tester, CC 24801
Minimum acceptable IR (MΩ) |  |  | 100 |  |  | Date |  |  | 2026-10-25
Insulation resistance results
No | Cable tag | From | To | Cores | Test voltage (V) | Core to core (MΩ) | Core to earth (MΩ) | Core to screen (MΩ) | Result | By | Remarks
1 | IC 2001 | PT 2101 | JB 2001 | 2 | 500 | 2000 | 2000 | 2000 | PASS | Tech A
2 | MC 2001 | JB 2001 | MAR 01 | 24 | 500 | 1500 | 1200 | 1100 | PASS | Tech A
3 | IC 2002 | TT 2102 | JB 2001 | 3 | 500 | 900 | 45 | 600 | FAIL | Tech A | Low to earth, water in gland
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
Cables tested | [9 empty] | 3
Cables failed | [9 empty] | 1
Disconnect cables from instruments and system cards before testing: test voltage can damage electronics. Discharge cores after testing. Use the minimum IR from your project specification.
Tested by |  |  |  | Witnessed by |  |  |  | Approved by
Name: |  |  |  | Name: |  |  |  | Name:
Signature: |  |  |  | Signature: |  |  |  | Signature:
Date: |  |  |  | Date: |  |  |  | Date: