## How to Use
HOW TO USE: CONTROL VALVE CALIBRATION REPORT (POSITIONER STROKE CHECK)
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the rated travel from the valve nameplate and the allowed position tolerance.
2. With the process isolated and the valve safe to stroke, inject each signal with a mA source or from the DCS.
3. Measure the stem travel with a scale or dial gauge (or read the positioner travel) and type it in As found travel (mm).
4. If errors exceed tolerance, run the positioner auto calibration or adjust zero and span, then record As left travel.
5. Time a full open and close stroke and complete the functional checks before returning the valve to service.
What the formulas do
• Signal (mA) = 4 + 16 × signal % ÷ 100.
• Position (%) = measured travel ÷ rated travel × 100.
• Error (%) = position % − signal %. PASS when within tolerance (as left values used when present).
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
CONTROL VALVE CALIBRATION REPORT (POSITIONER STROKE CHECK)
Company: Your Company Name / Logo |  |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Valve details
Tag number |  |  |  |  | Service
Valve type and size |  |  |  |  | Actuator action
Positioner make and model |  |  |  |  | Positioner serial no
Rated travel (mm) |  |  |  |  | Position tolerance (± % travel)
Air supply (bar) |  |  |  |  | Test date
Stroke check (direct acting: 4 mA closed, 20 mA open)
Signal (%) | Signal (mA) | As found travel (mm) | As found position (%) | As found error (%) | As left travel (mm) | As left position (%) | As left error (%) | Result
0 | 4
25 | 8
50 | 12
75 | 16
100 | 20
75 | 16
50 | 12
25 | 8
0 | 4
Maximum as left error (%)
Overall result
Stroke time and functional checks
Full stroke time, opening (s) |  |  |  |  | Full stroke time, closing (s)
Fail action on air loss correct? |  |  |  |  | Position feedback to DCS correct?
Air leaks checked? |  |  |  |  | Tight shut off at 0 %?
Performed by |  |  | Checked by |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:

## Example
CONTROL VALVE CALIBRATION REPORT (POSITIONER STROKE CHECK)
Company: ABC Process Industries Ltd |  |  |  |  | Doc no: CAL FV 3101 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Valve details
Tag number |  | FV 3101 |  |  | Service |  | Feed flow to column C 301
Valve type and size |  | Globe, 3", 300# |  |  | Actuator action |  | Air to open (fail close)
Positioner make and model |  | Fisher DVC6200 |  |  | Positioner serial no |  | DVC 551029
Rated travel (mm) |  | 40 |  |  | Position tolerance (± % travel) |  | 1
Air supply (bar) |  | 4 |  |  | Test date |  | 2026-10-12
Stroke check (direct acting: 4 mA closed, 20 mA open)
Signal (%) | Signal (mA) | As found travel (mm) | As found position (%) | As found error (%) | As left travel (mm) | As left position (%) | As left error (%) | Result
0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | PASS
25 | 8 | 10.9 | 27.25 | 2.25 | 10 | 25 | 0 | PASS
50 | 12 | 20.8 | 52 | 2 | 20.1 | 50.25 | 0.25 | PASS
75 | 16 | 30.7 | 76.75 | 1.75 | 30 | 75 | 0 | PASS
100 | 20 | 39.4 | 98.5 | -1.5 | 40 | 100 | 0 | PASS
75 | 16 | 30.9 | 77.25 | 2.25 | 30.1 | 75.25 | 0.25 | PASS
50 | 12 | 21.1 | 52.75 | 2.75 | 20.1 | 50.25 | 0.25 | PASS
25 | 8 | 11.2 | 28 | 3 | 10.1 | 25.25 | 0.25 | PASS
0 | 4 | 0.3 | 0.75 | 0.75 | 0 | 0 | 0 | PASS
Maximum as left error (%) | [7 empty] | 0.25
Overall result | [7 empty] | PASS
Stroke time and functional checks
Full stroke time, opening (s) |  | 6.5 |  |  | Full stroke time, closing (s) |  | 5.8
Fail action on air loss correct? |  | Yes |  |  | Position feedback to DCS correct? |  | Yes
Air leaks checked? |  | Yes |  |  | Tight shut off at 0 %? |  | Yes
Performed by |  |  | Checked by |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date: