## How to Use
HOW TO USE: DP TRANSMITTER CALIBRATION REPORT
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter tag, range in mbar and tolerance.
2. With the transmitter in service, close HP and LP valves, open the equaliser and record the zero at line pressure; then vent and record the zero at atmosphere.
3. Isolate, connect the pressure standard to the HP side and vent the LP side.
4. Apply each test point upscale and downscale and record the as found output.
5. Trim zero and span if any point fails, record as left values, and return the manifold to service in the correct sequence.
What the formulas do
• Applied DP = LRV + span × test point %.
• Expected output = 4 + 16 × test point % mA.
• Error (% span) = (measured − expected) ÷ 16 × 100.
• Static pressure zero shift = (zero at line pressure − zero at atmosphere) ÷ 16 × 100.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
DP TRANSMITTER CALIBRATION REPORT
Company: Your Company Name / Logo |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Instrument details
Tag number |  |  |  | Service
Make and model |  |  |  | Serial number
Calibrated range LRV (mbar) |  |  |  | Calibrated range URV (mbar)
Output function |  |  |  | Static pressure in service (bar g)
Tolerance (± % of span) |  |  |  | Manifold
Zero check and test equipment
Zero at atmosphere (mA) |  |  |  | Zero at line pressure, equaliser open (mA)
Static pressure zero shift (% span) |  |  |  | Pressure standard
Standard certificate no |  |  |  | Calibration date
Calibration results (5 point, upscale and downscale)
Test point (% of span) | Applied DP (mbar) | Expected output (mA) | As found output (mA) | As found error (% span) | As found result | As left output (mA) | As left error (% span) | As left result
0 |  | 4
25 |  | 8
50 |  | 12
75 |  | 16
100 |  | 20
75 |  | 16
50 |  | 12
25 |  | 8
0 |  | 4
Maximum as found error (% span)
Maximum as left error (% span)
Overall result (as left if adjusted, else as found)
Apply pressure to the HP side with the LP side vented. For square root transmitters, calibrate in linear mode or use the expected current for the square root output.
Performed by |  |  | Checked by |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:

## Example
DP TRANSMITTER CALIBRATION REPORT
Company: ABC Process Industries Ltd |  |  |  | Doc no: CAL PDT 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Instrument details
Tag number |  | FT 3105 |  | Service |  | Feed water flow
Make and model |  | Vendor DP transmitter |  | Serial number |  | DP 220781
Calibrated range LRV (mbar) |  | 0 |  | Calibrated range URV (mbar) |  | 250
Output function |  | Linear (square root in DCS) |  | Static pressure in service (bar g) |  | 16
Tolerance (± % of span) |  | 0.25 |  | Manifold |  | 3 valve
Zero check and test equipment
Zero at atmosphere (mA) |  | 4.002 |  | Zero at line pressure, equaliser open (mA) |  | 4.018
Static pressure zero shift (% span) |  | 0.1 |  | Pressure standard |  | Low range pressure module 0 to 1 bar
Standard certificate no |  | CC 24502 |  | Calibration date |  | 2026-10-25
Calibration results (5 point, upscale and downscale)
Test point (% of span) | Applied DP (mbar) | Expected output (mA) | As found output (mA) | As found error (% span) | As found result | As left output (mA) | As left error (% span) | As left result
0 | 0 | 4 | 4.018 | 0.1125 | PASS | 4.002 | 0.0125 | PASS
25 | 62.5 | 8 | 8.046 | 0.2875 | FAIL | 8.003 | 0.01875 | PASS
50 | 125 | 12 | 12.061 | 0.38125 | FAIL | 12.001 | 0.00625 | PASS
75 | 187.5 | 16 | 16.082 | 0.5125 | FAIL | 16.002 | 0.0125 | PASS
100 | 250 | 20 | 20.09 | 0.5625 | FAIL | 20.001 | 0.00625 | PASS
75 | 187.5 | 16 | 16.077 | 0.48125 | FAIL | 16.003 | 0.01875 | PASS
50 | 125 | 12 | 12.056 | 0.35 | FAIL | 12.002 | 0.0125 | PASS
25 | 62.5 | 8 | 8.04 | 0.25 | PASS | 8.002 | 0.0125 | PASS
0 | 0 | 4 | 4.016 | 0.1 | PASS | 4.001 | 0.00625 | PASS
Maximum as found error (% span) | [6 empty] | 0.5625
Maximum as left error (% span) | [6 empty] | 0.01875
Overall result (as left if adjusted, else as found) | [6 empty] | PASS
Apply pressure to the HP side with the LP side vented. For square root transmitters, calibrate in linear mode or use the expected current for the square root output.
Performed by |  |  | Checked by |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date: