## How to Use
HOW TO USE: DIFFERENTIAL PRESSURE TRANSMITTER DATA SHEET
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the service and process conditions, including static pressure, which sets the transmitter body rating.
2. Give the calibrated DP range from the flow element or level calculation, and the output function.
3. Specify seals and capillaries for hot, viscous or corrosive service, and the manifold type.
4. Choose the burnout direction so a failure drives the loop to the safe side.
5. Issue with the requisition for vendor completion.
What the formulas do
• No formulas: specification document laid out in sections like an ISA 20 style data sheet.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
DIFFERENTIAL PRESSURE TRANSMITTER DATA SHEET
Company: Your Company Name / Logo |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  |  | Revision
Date |  |  | Requisition no
Specification
No | Parameter |  | Value | Unit / notes
General
1 | Tag number
2 | Service (flow, level or DP)
3 | Line or equipment
4 | P&ID number
5 | Hazardous area
Process conditions
6 | Fluid
7 | Static pressure (normal / maximum)
8 | Operating temperature (normal / maximum)
9 | Design pressure / temperature
10 | Differential range required
11 | Output function (linear / square root)
Transmitter
12 | Sensor range (URL)
13 | Calibrated range
14 | Maximum static pressure rating
15 | Accuracy
16 | Diaphragm / wetted material
17 | Fill fluid
18 | Process connection
19 | Remote seals and capillary
Electronics
20 | Output
21 | Burnout direction
22 | Ex certification
23 | Enclosure (IP)
24 | Display
25 | Cable entry
Accessories
26 | Manifold (3 or 5 valve)
27 | Mounting bracket
28 | Condensate pots / seal pots
Purchase
29 | Manufacturer / model
30 | Quantity
State the static pressure and the output function clearly: square root in the transmitter and in the DCS at the same time is a common error.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date:

## Example
DIFFERENTIAL PRESSURE TRANSMITTER DATA SHEET
Company: ABC Process Industries Ltd |  |  | Doc no: DS PDT 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  | Boiler 3 upgrade | Revision | A
Date |  | 2026-10-24 | Requisition no | REQ INST 031
Specification
No | Parameter |  | Value |  | Unit / notes
General
1 | Tag number |  | PDT 3105
2 | Service (flow, level or DP) |  | Flow, orifice FE 3105
3 | Line or equipment |  | 6" Sch 40 feed line
4 | P&ID number |  | PID 300 01
5 | Hazardous area |  | Zone 2, IIB T3
Process conditions
6 | Fluid |  | Water
7 | Static pressure (normal / maximum) |  | 10 / 16 |  | bar g
8 | Operating temperature (normal / maximum) |  | 60 / 90 |  | °C
9 | Design pressure / temperature |  | 25 / 120 |  | bar g / °C
10 | Differential range required |  | 0 to 250 |  | mbar
11 | Output function (linear / square root) |  | Linear (square root in DCS)
Transmitter
12 | Sensor range (URL) |  | 620 |  | mbar
13 | Calibrated range |  | 0 to 250 |  | mbar
14 | Maximum static pressure rating |  | 160 |  | bar g
15 | Accuracy |  | ± 0.075 |  | % of span
16 | Diaphragm / wetted material |  | SS 316L
17 | Fill fluid |  | Silicone oil
18 | Process connection |  | 1/2" NPT female
19 | Remote seals and capillary |  | Not required
Electronics
20 | Output |  | 4 to 20 mA HART
21 | Burnout direction |  | Downscale (≤ 3.6 mA) |  | NAMUR NE43
22 | Ex certification |  | Ex nA IIC T4 Gc
23 | Enclosure (IP) |  | IP66/67
24 | Display |  | LCD, local
25 | Cable entry |  | M20 x 1.5
Accessories
26 | Manifold (3 or 5 valve) |  | 3 valve, SS 316, integral
27 | Mounting bracket |  | 2" pipe mount, SS
28 | Condensate pots / seal pots |  | Not required
Purchase
29 | Manufacturer / model |  | Vendor to specify
30 | Quantity |  | 1 |  | no
State the static pressure and the output function clearly: square root in the transmitter and in the DCS at the same time is a common error.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date: