## How to Use
HOW TO USE: ESD VALVE FULL STROKE TEST REPORT
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Obtain a permit and operations approval; put the valve in a safe state for testing (bypass the trip only if your procedure allows).
2. Enter the required closing and opening times from the SIF specification (safety requirements specification).
3. Initiate each stroke from the source shown and time it from command to limit switch change with a stopwatch or the SIS sequence of events.
4. Record feedback and travel quality; any No makes the trial fail.
5. Remove bypasses, return the valve to service and file the report against the SIF proof test record.
What the formulas do
• Limit = required closing time for Close trials, required opening time for Open trials.
• Result PASS when measured time ≤ limit and feedback and travel checks are not No.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
ESD VALVE FULL STROKE TEST REPORT
Company: Your Company Name / Logo |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Valve details
Tag number |  |  |  | Service
Valve type and size |  |  |  | Actuator
Fail action |  |  |  | SIF / SIL
Required closing time (s, max) |  |  |  | Required opening time (s, max)
Test date |  |  |  | Proof test interval
Stroke tests
Trial | Command | Initiated from | Measured time (s) | Limit (s) | Limit switch feedback OK? | Smooth travel, no sticking? | Result | Remarks
1 | Close |  |  | 0
2 | Open |  |  | 0
3 | Close |  |  | 0
4 | Open |  |  | 0
5 | Close |  |  | 0
6 | Open |  |  | 0
Slowest closing time (s)
Slowest opening time (s)
Overall result
Additional checks
Seat leak test done? |  |  |  | Solenoid valve vents correctly?
Air supply pressure (bar) |  |  |  | Bypass / override removed after test?
Tested by |  |  | Witnessed by (operations) |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:

## Example
ESD VALVE FULL STROKE TEST REPORT
Company: ABC Process Industries Ltd |  |  |  | Doc no: PT XV4101 2026 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Valve details
Tag number |  | XV 4101 |  | Service |  | Tank inlet shutdown valve
Valve type and size |  | Ball valve, 6", 150#, fire safe |  | Actuator |  | Spring return, scotch yoke
Fail action |  | Fail close |  | SIF / SIL |  | SIF 04, SIL 1
Required closing time (s, max) |  | 10 |  | Required opening time (s, max) |  | 15
Test date |  | 2026-10-12 |  | Proof test interval |  | 12 months
Stroke tests
Trial | Command | Initiated from | Measured time (s) | Limit (s) | Limit switch feedback OK? | Smooth travel, no sticking? | Result | Remarks
1 | Close | SIS logic | 7.8 | 10 | Yes | Yes | PASS
2 | Open | DCS | 11.2 | 15 | Yes | Yes | PASS
3 | Close | Local push button | 7.9 | 10 | Yes | Yes | PASS
4 | Open | DCS | 11 | 15 | Yes | Yes | PASS
5 | Close | SIS logic | 7.7 | 10 | Yes | Yes | PASS
6 | Open | DCS | 11.1 | 15 | Yes | Yes | PASS
Slowest closing time (s) | [6 empty] | 7.9
Slowest opening time (s) | [6 empty] | 11.2
Overall result | [6 empty] | PASS
Additional checks
Seat leak test done? |  | Yes, Class VI, no visible leak |  | Solenoid valve vents correctly? |  | Yes
Air supply pressure (bar) |  | 5.5 |  | Bypass / override removed after test? |  | Yes
Tested by |  |  | Witnessed by (operations) |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date: