## How to Use
HOW TO USE: EX EQUIPMENT INSPECTION CHECKLIST
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the equipment details from the Ex register, including the area classification and certificate number.
2. Select the inspection grade (visual, close or detailed) and type (initial, periodic or sample).
3. Check each item and select OK, Not OK or NA. Items that do not apply to the protection type are NA.
4. Write a remark and raise a work order for every Not OK item.
5. The equipment result shows FAIL while any item is Not OK.
What the formulas do
• Items not OK = count of "Not OK".
• Equipment result = FAIL if any item is Not OK, otherwise PASS.
• Next inspection due = inspection date + 36 months (edit to suit your interval).
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
EX EQUIPMENT INSPECTION CHECKLIST
Company: Your Company Name / Logo |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Equipment
Tag number |  |  | Equipment
Location |  |  | Area classification
Ex marking |  |  | Certificate no
Inspection grade |  |  | Inspection type
Inspection date |  |  | Next inspection due
Inspection items
No | Check item |  |  | Status | Remarks
1 | Equipment protection level (EPL) suitable for the zone
2 | Equipment group (IIA, IIB, IIC or IIIA, IIIB, IIIC) suitable for the area
3 | Temperature class or maximum surface temperature suitable for the gas or dust
4 | Ex marking and certificate number legible and match the register
5 | Circuit identification and tag plate correct
6 | Enclosure, windows and seals free of damage, corrosion and cracks
7 | No unauthorised modifications or visible changes
8 | All bolts, screws and covers present and tight
9 | Cable entries: glands of the correct Ex type, size and tight
10 | Unused entries closed with certified stopping plugs
11 | Cables free of damage; armour and screens terminated correctly
12 | Earthing and equipotential bonding connections secure
13 | Ex d: flame path free of damage, corrosion and paint; no obstruction near flanges
14 | Ex e: terminals tight, no damaged insulation, correct number of conductors per terminal
15 | Ex i: barriers or isolators of the correct type; IS cables identified and segregated
16 | No dust build up or water ingress inside or on the equipment
17 | Lamps, fans or heaters of the correct type and rating (where fitted)
18 | Protection settings (overload, motor tE time) correct (where fitted)
Items not OK |  |  |  |  | 0
Equipment result
Next inspection due assumes a 36 month interval; set your own interval from the site inspection strategy. Detailed inspections may need the equipment isolated and opened by a competent person.
Inspected by (competent person) |  | Reviewed by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date:

## Example
EX EQUIPMENT INSPECTION CHECKLIST
Company: ABC Process Industries Ltd |  |  | Doc no: EXI 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Equipment
Tag number |  | PT 1101 | Equipment |  | Pressure transmitter
Location |  | Boiler house, EL +6 m | Area classification |  | Zone 1, IIB T3
Ex marking |  | Ex db IIC T6 Gb | Certificate no |  | IECEx XXX 12.0034X
Inspection grade |  | Close | Inspection type |  | Periodic
Inspection date |  | 2026-10-14 | Next inspection due |  | 2029-10-14
Inspection items
No | Check item |  |  | Status | Remarks
1 | Equipment protection level (EPL) suitable for the zone |  |  | OK
2 | Equipment group (IIA, IIB, IIC or IIIA, IIIB, IIIC) suitable for the area |  |  | OK
3 | Temperature class or maximum surface temperature suitable for the gas or dust |  |  | OK
4 | Ex marking and certificate number legible and match the register |  |  | OK
5 | Circuit identification and tag plate correct |  |  | OK
6 | Enclosure, windows and seals free of damage, corrosion and cracks |  |  | OK
7 | No unauthorised modifications or visible changes |  |  | OK
8 | All bolts, screws and covers present and tight |  |  | OK
9 | Cable entries: glands of the correct Ex type, size and tight |  |  | Not OK | Gland loose, retighten and check seal
10 | Unused entries closed with certified stopping plugs |  |  | OK
11 | Cables free of damage; armour and screens terminated correctly |  |  | OK
12 | Earthing and equipotential bonding connections secure |  |  | OK
13 | Ex d: flame path free of damage, corrosion and paint; no obstruction near flanges |  |  | OK
14 | Ex e: terminals tight, no damaged insulation, correct number of conductors per terminal |  |  | NA | Ex d equipment
15 | Ex i: barriers or isolators of the correct type; IS cables identified and segregated |  |  | NA | Not intrinsically safe
16 | No dust build up or water ingress inside or on the equipment |  |  | OK
17 | Lamps, fans or heaters of the correct type and rating (where fitted) |  |  | NA
18 | Protection settings (overload, motor tE time) correct (where fitted) |  |  | NA
Items not OK |  |  |  |  | 1
Equipment result |  |  |  |  | FAIL
Next inspection due assumes a 36 month interval; set your own interval from the site inspection strategy. Detailed inspections may need the equipment isolated and opened by a competent person.
Inspected by (competent person) |  | Reviewed by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date: