## How to Use
HOW TO USE: FACTORY ACCEPTANCE TEST (FAT) CHECKLIST: CONTROL PANEL AND DCS / PLC
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Agree the FAT procedure and this checklist with the vendor before the test date. Add or remove rows to suit your system.
2. Fill the project details and test each item in order, witnessed by the client.
3. Select PASS, FAIL or NA for every row and write remarks for FAIL and NA items.
4. Every FAIL becomes a punch item; retest and update the result once fixed.
5. Sign the checklist when the FAT status shows PASS or the open items are agreed in the punch list.
What the formulas do
• Counts of PASS, FAIL, NA and untested rows.
• FAT status is FAIL if any row failed, CHECK while rows are untested, otherwise PASS.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
FACTORY ACCEPTANCE TEST (FAT) CHECKLIST: CONTROL PANEL AND DCS / PLC
Company: Your Company Name / Logo |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Project
Project |  |  |  | Client
System / panel |  |  |  | Vendor
PO number |  |  |  | FAT date
Location |  |  |  | FAT procedure
Test checklist
No | Section | Check item |  |  | Acceptance criteria |  | Result | Remarks
1 | Documentation | Approved drawings, I/O list and FAT procedure available |  |  | Latest revision on file
2 | Documentation | Bill of materials matches supplied hardware |  |  | Make, model and quantity match
3 | Visual | Panel dimensions, colour, IP rating and nameplates |  |  | As per approved GA drawing
4 | Visual | Wiring neat, ferruled, colour coded, segregated (IS / non IS, AC / DC) |  |  | No damage, loose strands or mix
5 | Visual | Earth bars (PE, IE / clean earth) and bonding |  |  | Separate bars, all doors bonded
6 | Power | Insulation resistance of incoming power circuits |  |  | ≥ 1 MΩ at 500 V DC
7 | Power | Power on; all supply voltages measured |  |  | Within ± 5 % of nominal
8 | Power | Redundant power supply changeover |  |  | No interruption to controllers
9 | Hardware | Controllers, I/O cards and network switches healthy |  |  | No diagnostic alarms
10 | I/O test | Analog inputs: 4, 12, 20 mA injected on every channel |  |  | Reading within ± 0.25 % of span
11 | I/O test | Analog outputs: 0, 50, 100 % from HMI measured |  |  | Within ± 0.25 % of span
12 | I/O test | Digital inputs: every channel toggled |  |  | Correct tag changes state on HMI
13 | I/O test | Digital outputs: every channel forced |  |  | Correct relay / terminal energises
14 | I/O test | Open circuit and short circuit detection on AI channels |  |  | Bad PV alarm raised
15 | Communication | Fieldbus / Modbus / Ethernet links to third party systems |  |  | Data exchange verified, failure alarm works
16 | Communication | Network redundancy: one cable pulled |  |  | No loss of view or control
17 | Logic | Control loops: modes, PID action and output limits |  |  | As per control narrative
18 | Logic | Interlocks and sequences tested against cause and effect |  |  | Every cause gives the correct effect
19 | HMI | Graphics, tag names, units and ranges checked |  |  | Match I/O list
20 | HMI | Alarm priorities, set points and alarm summary |  |  | Match alarm list
21 | HMI | User security levels and login |  |  | Operator / engineer rights correct
22 | Redundancy | Controller failover (primary pulled or powered off) |  |  | Bumpless, no output change
23 | Final | Backups of application and configuration taken |  |  | Copy handed to client
24 | Final | Punch list agreed and signed |  |  | No category A items open
PASS | [6 empty] | 0
FAIL | [6 empty] | 0
Not applicable | [6 empty] | 0
Not yet tested | [6 empty] | 24
FAT status
Vendor |  |  | Client |  |  | Third party inspector
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:

## Example
FACTORY ACCEPTANCE TEST (FAT) CHECKLIST: CONTROL PANEL AND DCS / PLC
Company: ABC Process Industries Ltd |  |  |  | Doc no: FAT CP 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Project
Project |  | Boiler 3 control system upgrade |  | Client |  | ABC Process Industries Ltd
System / panel |  | PLC panel CP 03 and 2 HMI stations |  | Vendor |  | XYZ Automation Pvt Ltd
PO number |  | PO/4501/2026 |  | FAT date |  | 2026-10-12
Location |  | Vendor works, Pune |  | FAT procedure |  | FAT PROC 03 Rev 1
Test checklist
No | Section | Check item |  |  | Acceptance criteria |  | Result | Remarks
1 | Documentation | Approved drawings, I/O list and FAT procedure available |  |  | Latest revision on file |  | PASS
2 | Documentation | Bill of materials matches supplied hardware |  |  | Make, model and quantity match |  | PASS
3 | Visual | Panel dimensions, colour, IP rating and nameplates |  |  | As per approved GA drawing |  | PASS
4 | Visual | Wiring neat, ferruled, colour coded, segregated (IS / non IS, AC / DC) |  |  | No damage, loose strands or mix |  | PASS
5 | Visual | Earth bars (PE, IE / clean earth) and bonding |  |  | Separate bars, all doors bonded |  | PASS
6 | Power | Insulation resistance of incoming power circuits |  |  | ≥ 1 MΩ at 500 V DC |  | PASS
7 | Power | Power on; all supply voltages measured |  |  | Within ± 5 % of nominal |  | PASS
8 | Power | Redundant power supply changeover |  |  | No interruption to controllers |  | PASS
9 | Hardware | Controllers, I/O cards and network switches healthy |  |  | No diagnostic alarms |  | PASS
10 | I/O test | Analog inputs: 4, 12, 20 mA injected on every channel |  |  | Reading within ± 0.25 % of span |  | PASS
11 | I/O test | Analog outputs: 0, 50, 100 % from HMI measured |  |  | Within ± 0.25 % of span |  | PASS
12 | I/O test | Digital inputs: every channel toggled |  |  | Correct tag changes state on HMI |  | PASS
13 | I/O test | Digital outputs: every channel forced |  |  | Correct relay / terminal energises |  | PASS
14 | I/O test | Open circuit and short circuit detection on AI channels |  |  | Bad PV alarm raised |  | FAIL | CH 7 to 12 of AI 02 no open circuit alarm; config fix, retest
15 | Communication | Fieldbus / Modbus / Ethernet links to third party systems |  |  | Data exchange verified, failure alarm works |  | NA | No third party link
16 | Communication | Network redundancy: one cable pulled |  |  | No loss of view or control |  | PASS
17 | Logic | Control loops: modes, PID action and output limits |  |  | As per control narrative |  | PASS
18 | Logic | Interlocks and sequences tested against cause and effect |  |  | Every cause gives the correct effect |  | PASS
19 | HMI | Graphics, tag names, units and ranges checked |  |  | Match I/O list |  | PASS
20 | HMI | Alarm priorities, set points and alarm summary |  |  | Match alarm list |  | PASS
21 | HMI | User security levels and login |  |  | Operator / engineer rights correct |  | PASS
22 | Redundancy | Controller failover (primary pulled or powered off) |  |  | Bumpless, no output change |  | PASS
23 | Final | Backups of application and configuration taken |  |  | Copy handed to client |  | PASS
24 | Final | Punch list agreed and signed |  |  | No category A items open |  | PASS
PASS | [6 empty] | 22
FAIL | [6 empty] | 1
Not applicable | [6 empty] | 1
Not yet tested | [6 empty] | 0
FAT status | [6 empty] | FAIL
Vendor |  |  | Client |  |  | Third party inspector
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date: