## How to Use
HOW TO USE: FIXED GAS DETECTOR DATA SHEET
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the target gas and its LEL or exposure limit and relative density.
2. Choose the technology for the gas and environment (IR for hydrocarbons, catalytic for hydrogen and mixed gases, electrochemical for toxics).
3. Set the range and alarm levels from the fire and gas philosophy.
4. Specify mounting, calibration access and outputs.
5. Issue with the requisition.
What the formulas do
• No formulas: specification document laid out in sections like an ISA 20 style data sheet.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
FIXED GAS DETECTOR DATA SHEET
Company: Your Company Name / Logo |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  |  | Revision
Date |  |  | Requisition no
Specification
No | Parameter |  | Value | Unit / notes
General
1 | Tag number
2 | Location / area
3 | Detection purpose (leak, area, duct)
4 | Hazardous area
Gas
5 | Target gas
6 | LEL or exposure limit
7 | Gas density relative to air
8 | Mounting height (calculated hint)
Detector
9 | Technology (catalytic, IR, electrochemical, open path)
10 | Measuring range
11 | Alarm set points (low / high)
12 | Response time (T90)
13 | Ex certification
14 | SIL capability
Installation
15 | Mounting
16 | Calibration adapter / remote test
17 | Weather or splash guard
Outputs
18 | Signal
19 | Relays
20 | Power supply
21 | Cable entry
Purchase
22 | Manufacturer / model
23 | Quantity
Mounting height depends on gas density and the release scenario: lighter than air gases are detected high, heavier gases low. Confirm detector positions with a gas mapping or dispersion study.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date:

## Example
FIXED GAS DETECTOR DATA SHEET
Company: ABC Process Industries Ltd |  |  | Doc no: DS GD 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  | Boiler 3 upgrade | Revision | A
Date |  | 2026-10-24 | Requisition no | REQ INST 034
Specification
No | Parameter |  | Value |  | Unit / notes
General
1 | Tag number |  | GD 2201
2 | Location / area |  | Compressor house, near seals
3 | Detection purpose (leak, area, duct) |  | Leak detection
4 | Hazardous area |  | Zone 1, IIA T3
Gas
5 | Target gas |  | Methane
6 | LEL or exposure limit |  | 4.4 % vol (LEL) |  | IEC 60079-20-1
7 | Gas density relative to air |  | 0.55 |  | air = 1
8 | Mounting height (calculated hint) |  | High: lighter than air |  | confirm with dispersion study
Detector
9 | Technology (catalytic, IR, electrochemical, open path) |  | Infrared point
10 | Measuring range |  | 0 to 100 |  | % LEL
11 | Alarm set points (low / high) |  | 20 / 40 |  | % LEL
12 | Response time (T90) |  | < 10 |  | s
13 | Ex certification |  | Ex db IIC T4 Gb
14 | SIL capability |  | SIL 2
Installation
15 | Mounting |  | Wall, 0.5 m below roof
16 | Calibration adapter / remote test |  | Yes, flow cap
17 | Weather or splash guard |  | Yes
Outputs
18 | Signal |  | 4 to 20 mA HART
19 | Relays |  | Not required
20 | Power supply |  | 24 V DC
21 | Cable entry |  | M20 x 1.5
Purchase
22 | Manufacturer / model |  | Vendor to specify
23 | Quantity |  | 1 |  | no
Mounting height depends on gas density and the release scenario: lighter than air gases are detected high, heavier gases low. Confirm detector positions with a gas mapping or dispersion study.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date: