## How to Use
HOW TO USE: INSTRUMENTATION SYSTEM HANDOVER CERTIFICATE
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Define the system and scope being handed over.
2. Go through the checklist with both parties and mark each item.
3. Enter the open punch counts; any category A item blocks handover.
4. List exceptions with dates in the remarks.
5. Sign by the handing and receiving parties.
What the formulas do
• Ready = NOT READY while any category A punch item is open.
• Items not OK counted at the bottom.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
INSTRUMENTATION SYSTEM HANDOVER CERTIFICATE
Company: Your Company Name / Logo |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
System
System / subsystem |  |  | Scope
Handed over by |  |  | Received by
Handover date |  |  | Open category A punch items
Open category B punch items |  |  | Ready for handover?
Handover checklist
No | Check item |  |  | Status | Remarks
1 | Installation checklist completed and signed
2 | Calibration certificates available for all instruments
3 | Cold loop check completed
4 | Hot loop check completed with operations
5 | Control valves stroked and positioners tuned
6 | Alarms and trips tested; cause and effect verified
7 | Punch list: no category A items open
8 | As built P&IDs, loop drawings and instrument index issued
9 | Data sheets and vendor manuals handed over
10 | Configuration backups of DCS, PLC and smart instruments
11 | Spare parts handed over and listed
12 | Training of operations and maintenance completed
Items not OK |  |  |  |  | 0
Category A punch items must be closed before handover; category B items may be accepted with an agreed completion date. Attach the punch list and the list of exceptions.
Construction / contractor |  | Commissioning | Operations (accepting)
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date:

## Example
INSTRUMENTATION SYSTEM HANDOVER CERTIFICATE
Company: ABC Process Industries Ltd |  |  | Doc no: HO INST 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
System
System / subsystem |  | SYS 300 Feed system | Scope |  | All field instruments and loops of SYS 300
Handed over by |  | Construction | Received by |  | Commissioning
Handover date |  | 2026-10-24 | Open category A punch items |  | 0
Open category B punch items |  | 3 | Ready for handover? |  | READY (with B punch)
Handover checklist
No | Check item |  |  | Status | Remarks
1 | Installation checklist completed and signed |  |  | OK
2 | Calibration certificates available for all instruments |  |  | OK
3 | Cold loop check completed |  |  | OK
4 | Hot loop check completed with operations |  |  | OK
5 | Control valves stroked and positioners tuned |  |  | OK
6 | Alarms and trips tested; cause and effect verified |  |  | OK
7 | Punch list: no category A items open |  |  | OK
8 | As built P&IDs, loop drawings and instrument index issued |  |  | Not OK | As built loop drawings to follow within 30 days
9 | Data sheets and vendor manuals handed over |  |  | OK
10 | Configuration backups of DCS, PLC and smart instruments |  |  | OK
11 | Spare parts handed over and listed |  |  | OK
12 | Training of operations and maintenance completed |  |  | OK
Items not OK |  |  |  |  | 1
Category A punch items must be closed before handover; category B items may be accepted with an agreed completion date. Attach the punch list and the list of exceptions.
Construction / contractor |  | Commissioning | Operations (accepting)
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date: