## How to Use
HOW TO USE: INSTRUMENT INSTALLATION CHECKLIST
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Fill in the instrument and area details, including the hazardous area classification.
2. Inspect each item in the field and select OK, Not OK or NA. Add a remark for every Not OK.
3. Raise a punch item for every Not OK (see the punch list template).
4. Reinspect after correction; the sheet shows OK when no items remain Not OK.
What the formulas do
• Items not OK = count of "Not OK".
• Ready for loop check shows CHECK while any item is Not OK.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
INSTRUMENT INSTALLATION CHECKLIST
Company: Your Company Name / Logo |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Instrument
Tag number |  |  | Instrument type
Service |  |  | Hook up drawing
Area / location |  |  | Hazardous area
Make and model |  |  | Inspection date
Installation checks
No | Check item |  |  | Status | Remarks
1 | Correct instrument installed (tag, model, range and material match data sheet)
2 | Tag plate fixed and legible
3 | Mounted as per hook up drawing, accessible for maintenance
4 | Mounting bracket or stand secure, free from vibration
5 | Process connection orientation correct (gas: above tap, liquid: below tap)
6 | Impulse lines sloped correctly (1:12 minimum) and supported
7 | Manifold / isolation valves fitted and operable
8 | Impulse lines and fittings pressure tested and leak free
9 | Seal pots, condensate pots or diaphragm seals filled as required
10 | Cable gland type and size correct, Ex certified for the zone
11 | Cable entry sealed, unused entries plugged with certified plugs
12 | Cable supported, protected and identified at both ends
13 | Enclosure cover, O ring and seals intact (IP rating maintained)
14 | Earth / equipotential bonding connected
15 | Sun shade or weather protection fitted where specified
16 | Heat tracing and insulation installed where specified
Items not OK |  |  |  |  | 0
Ready for loop check?
Installed by |  | Inspected by | Client QA/QC
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date:

## Example
INSTRUMENT INSTALLATION CHECKLIST
Company: ABC Process Industries Ltd |  |  | Doc no: IIC FT 3101 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Instrument
Tag number |  | PDT 3105 | Instrument type |  | DP transmitter (flow, orifice)
Service |  | Feed flow to column C 301 | Hook up drawing |  | HU DP LIQ 03
Area / location |  | Column area, EL +3.5 m | Hazardous area |  | Zone 2, IIB T3
Make and model |  | Yokogawa EJA110E | Inspection date |  | 2026-10-12
Installation checks
No | Check item |  |  | Status | Remarks
1 | Correct instrument installed (tag, model, range and material match data sheet) |  |  | OK
2 | Tag plate fixed and legible |  |  | OK
3 | Mounted as per hook up drawing, accessible for maintenance |  |  | OK
4 | Mounting bracket or stand secure, free from vibration |  |  | OK
5 | Process connection orientation correct (gas: above tap, liquid: below tap) |  |  | OK
6 | Impulse lines sloped correctly (1:12 minimum) and supported |  |  | OK
7 | Manifold / isolation valves fitted and operable |  |  | OK
8 | Impulse lines and fittings pressure tested and leak free |  |  | OK
9 | Seal pots, condensate pots or diaphragm seals filled as required |  |  | OK
10 | Cable gland type and size correct, Ex certified for the zone |  |  | Not OK | M20 gland on M25 entry, replace with M25 Ex d gland
11 | Cable entry sealed, unused entries plugged with certified plugs |  |  | OK
12 | Cable supported, protected and identified at both ends |  |  | OK
13 | Enclosure cover, O ring and seals intact (IP rating maintained) |  |  | OK
14 | Earth / equipotential bonding connected |  |  | OK
15 | Sun shade or weather protection fitted where specified |  |  | NA | Not specified
16 | Heat tracing and insulation installed where specified |  |  | NA
Items not OK |  |  |  |  | 1
Ready for loop check? |  |  |  |  | CHECK
Installed by |  | Inspected by | Client QA/QC
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date: