## How to Use
HOW TO USE: INSTRUMENT FAILURE ROOT CAUSE ANALYSIS
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Describe the event and its impact factually.
2. Ask why up to five times until you reach a cause you can fix in the system.
3. Pick the root cause category.
4. Agree corrective actions with owners and due dates.
5. Track actions to closure; status updates automatically.
What the formulas do
• Status: Closed when a done date is entered; OVERDUE when past due; otherwise Open.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
INSTRUMENT FAILURE ROOT CAUSE ANALYSIS
Company: Your Company Name / Logo |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Event
Instrument tag |  |  |  | Date of event
What happened |  |  |  | Impact
Root cause category |  |  |  | Team
5 why analysis
Why | Question |  |  | Answer
1
2
3
4
5
Corrective actions
No | Action |  | Owner | Due | Done | Status | Remarks
1
2
3
4
5
6
7
8
Open actions | [5 empty] | 0
Overdue | [5 empty] | 0
Investigated by |  | Reviewed by |  | Approved by
Name: |  | Name: |  | Name:
Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date:
Formulas:
Status = IF([Question]="","",IF([Done]<>"","Closed",IF(AND([Answer]<>"",TODAY()>[Answer]),"OVERDUE","Open")))

## Example
INSTRUMENT FAILURE ROOT CAUSE ANALYSIS
Company: ABC Process Industries Ltd |  |  |  | Doc no: RCA 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Event
Instrument tag |  | LT 2101 |  | Date of event |  | 2026-10-18
What happened |  | Drum level read 20 % high; high level alarm missed real low level |  | Impact |  | Boiler trip on low level, 4 h downtime
Root cause category |  | Maintenance |  | Team |  | Instrument, operations, process
5 why analysis
Why | Question |  |  | Answer
1 | Why did level read high? |  |  | Wet leg on LP side had partly drained
2 | Why did the wet leg drain? |  |  | Leaking vent valve on the condensate pot
3 | Why was the leak not found? |  |  | Wet leg check not in the PM schedule
4 | Why was it not in the schedule? |  |  | PM template copied from dry leg transmitters
5 | Why was the template not reviewed? |  |  | No review step when PMs are created
Corrective actions
No | Action |  | Owner | Due | Done | Status | Remarks
1 | Replace vent valve and refill wet leg |  | Instrument | 2026-10-19 | 2026-10-18 | Closed
2 | Add wet leg checks to PM for all wet leg loops |  | Maintenance planner | 2026-11-13 |  | Open
3 | Add review step for new PM templates |  | Maintenance manager | 2026-11-23 |  | Open
4
5
6
7
8
Open actions | [5 empty] | 2
Overdue | [5 empty] | 0
Investigated by |  | Reviewed by |  | Approved by
Name: |  | Name: |  | Name:
Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date:
Formulas:
Boiler trip on low level, 4 h downtime = IF([Question]="","",IF([Done]<>"","Closed",IF(AND([Date of event]<>"",TODAY()>[Date of event]),"OVERDUE","Open")))