## How to Use
HOW TO USE: INSTRUMENT JUNCTION BOX DATA SHEET
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Define location, area classification and signal type.
2. Choose enclosure material, size, IP and Ex protection.
3. Count terminals including spares and earth requirements.
4. List gland entries by cable size.
5. Add labelling and test requirements.
What the formulas do
• No formulas: specification document laid out in sections like an ISA 20 style data sheet.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
INSTRUMENT JUNCTION BOX DATA SHEET
Company: Your Company Name / Logo |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  |  | Revision
Date |  |  | Requisition no
Specification
No | Parameter |  | Value | Unit / notes
General
1 | Tag number
2 | Area / location
3 | Hazardous area
4 | Signal type (analog, digital, IS, fieldbus)
Enclosure
5 | Material
6 | Size (H x W x D)
7 | Ingress protection
8 | Ex protection
9 | Mounting
10 | Door / cover
11 | Breather and drain
Internals
12 | Terminal type and size
13 | Number of terminals (incl. spares)
14 | Earth bar / IS earth
15 | Cable glands (number and size)
16 | Gland plate
Labels and tests
17 | Labels
18 | Factory tests
Purchase
19 | Manufacturer / model
20 | Quantity
Keep IS and non IS signals in separate boxes or segregated compartments, and allow at least 20 % spare terminals.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date:

## Example
INSTRUMENT JUNCTION BOX DATA SHEET
Company: ABC Process Industries Ltd |  |  | Doc no: DS JB 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  | Boiler 3 upgrade | Revision | A
Date |  | 2026-10-24 | Requisition no | REQ INST 038
Specification
No | Parameter |  | Value |  | Unit / notes
General
1 | Tag number |  | JB 2001
2 | Area / location |  | Area 200, pipe rack
3 | Hazardous area |  | Zone 2, IIB T4
4 | Signal type (analog, digital, IS, fieldbus) |  | Analog 4 to 20 mA, non IS
Enclosure
5 | Material |  | SS 316L
6 | Size (H x W x D) |  | 400 x 300 x 200 |  | mm
7 | Ingress protection |  | IP66
8 | Ex protection |  | Ex eb IIC T6 Gb
9 | Mounting |  | Wall / stand
10 | Door / cover |  | Hinged, padlockable
11 | Breather and drain |  | Yes
Internals
12 | Terminal type and size |  | 2.5 mm² feed through
13 | Number of terminals (incl. spares) |  | 48 (20 % spare)
14 | Earth bar / IS earth |  | Isolated instrument earth bar
15 | Cable glands (number and size) |  | 12 x M20, 2 x M32
16 | Gland plate |  | Removable, bottom entry
Labels and tests
17 | Labels |  | Tag plate and terminal markers
18 | Factory tests |  | Dielectric and visual
Purchase
19 | Manufacturer / model |  | Vendor to specify
20 | Quantity |  | 1 |  | no
Keep IS and non IS signals in separate boxes or segregated compartments, and allow at least 20 % spare terminals.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date: