## How to Use
HOW TO USE: DP LEVEL TRANSMITTER CALIBRATION REPORT
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter LRV and URV in mbar as calculated for the tank, including wet leg or seal head.
2. Enter process SG to see the equivalent level for each test point.
3. Apply DP at the HP side (or apply vacuum to the LP side for negative values) and record outputs upscale and downscale.
4. Adjust if needed and record as left readings.
5. Restore wet legs and seals before returning to service.
What the formulas do
• Applied DP = LRV + span × test point %.
• Equivalent level (m) = (applied DP − LRV) × 100 ÷ (SG × 9806.65).
• Error (% span) = (measured − expected mA) ÷ 16 × 100.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
DP LEVEL TRANSMITTER CALIBRATION REPORT
Company: Your Company Name / Logo |  |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Instrument details
Tag number |  |  |  |  | Service
LRV (mbar), negative for elevated zero |  |  |  |  | URV (mbar)
Process specific gravity |  |  |  |  | Low side
Tolerance (± % of span) |  |  |  |  | Calibration date
Calibration results
Test point (% of span) | Applied DP (mbar) | Equivalent level (m) | Expected output (mA) | As found output (mA) | As found error (% span) | As found result | As left output (mA) | As left error (% span) | As left result
0 |  |  | 4
25 |  |  | 8
50 |  |  | 12
75 |  |  | 16
100 |  |  | 20
75 |  |  | 16
50 |  |  | 12
25 |  |  | 8
0 |  |  | 4
Maximum as found error (% span)
Maximum as left error (% span)
Overall result (as left if adjusted, else as found)
For wet leg systems, the LRV is negative: with an empty tank the wet leg head on the LP side gives a negative DP. Check the wet leg is full before calibration.
Performed by |  |  | Checked by |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:

## Example
DP LEVEL TRANSMITTER CALIBRATION REPORT
Company: ABC Process Industries Ltd |  |  |  |  | Doc no: CAL LT 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Instrument details
Tag number |  | LT 2101 |  |  | Service |  | Condensate drum level
LRV (mbar), negative for elevated zero |  | -294.2 |  |  | URV (mbar) |  | 0
Process specific gravity |  | 1 |  |  | Low side |  | Wet leg, water, 3 m
Tolerance (± % of span) |  | 0.25 |  |  | Calibration date |  | 2026-10-25
Calibration results
Test point (% of span) | Applied DP (mbar) | Equivalent level (m) | Expected output (mA) | As found output (mA) | As found error (% span) | As found result | As left output (mA) | As left error (% span) | As left result
0 | -294.2 | 0 | 4 | 4.01 | 0.0625 | PASS | 4.001 | 0.00625 | PASS
25 | -220.65 | 0.75 | 8 | 8.021 | 0.13125 | PASS | 8.002 | 0.0125 | PASS
50 | -147.1 | 1.5 | 12 | 12.03 | 0.1875 | PASS | 12.001 | 0.00625 | PASS
75 | -73.55 | 2.25 | 16 | 16.041 | 0.25625 | FAIL | 16.001 | 0.00625 | PASS
100 | 0 | 3 | 20 | 20.05 | 0.3125 | FAIL | 20.002 | 0.0125 | PASS
75 | -73.55 | 2.25 | 16 | 16.038 | 0.2375 | PASS | 16.002 | 0.0125 | PASS
50 | -147.1 | 1.5 | 12 | 12.027 | 0.16875 | PASS | 12.001 | 0.00625 | PASS
25 | -220.65 | 0.75 | 8 | 8.019 | 0.11875 | PASS | 8.001 | 0.00625 | PASS
0 | -294.2 | 0 | 4 | 4.008 | 0.05 | PASS | 4 | 0 | PASS
Maximum as found error (% span) | [7 empty] | 0.3125
Maximum as left error (% span) | [7 empty] | 0.0125
Overall result (as left if adjusted, else as found) | [7 empty] | PASS
For wet leg systems, the LRV is negative: with an empty tank the wet leg head on the LP side gives a negative DP. Check the wet leg is full before calibration.
Performed by |  |  | Checked by |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date: