## How to Use
HOW TO USE: LEVEL TRANSMITTER DATA SHEET
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter vessel, liquid and operating data, including minimum and maximum density.
2. Add the properties the chosen principle depends on: dielectric constant for radar and GWR, density for DP and displacer.
3. Define the measuring range and its reference point (usually the vessel bottom or tangent line).
4. Specify nozzle, probe or antenna, materials, output and Ex certification.
5. Issue with the requisition for vendor completion.
What the formulas do
• Range in % of vessel = measuring range ÷ vessel height × 100.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
LEVEL TRANSMITTER DATA SHEET
Company: Your Company Name / Logo |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  |  | Revision
Date |  |  | Requisition no
Specification
No | Parameter |  | Value | Unit / notes
General
1 | Tag number
2 | Service
3 | Vessel / tank
4 | Vessel height
5 | P&ID number
6 | Hazardous area
Process conditions
7 | Liquid
8 | Density (minimum / maximum)
9 | Dielectric constant
10 | Operating pressure / temperature
11 | Design pressure / temperature
12 | Foam, turbulence or coating
13 | Vapour or dust in the space above
Measurement
14 | Measuring principle
15 | Nozzle size / height
16 | Measuring range (from reference)
17 | Range in % of vessel (calculated)
18 | Interface measurement
19 | Accuracy
20 | Probe / antenna length
21 | Wetted materials
22 | Stilling well / bypass chamber
Transmitter
23 | Output
24 | Ex certification
25 | Enclosure (IP)
26 | Display
27 | Cable entry
Purchase
28 | Manufacturer / model
29 | Quantity
Give density for DP and displacer meters, dielectric constant for radar and capacitance, and note foam, turbulence and coating: they decide which principle will work.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date:

## Example
LEVEL TRANSMITTER DATA SHEET
Company: ABC Process Industries Ltd |  |  | Doc no: DS LT 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  | Tank farm upgrade | Revision | A
Date |  | 2026-10-14 | Requisition no | REQ INST 022
Specification
No | Parameter |  | Value |  | Unit / notes
General
1 | Tag number |  | LT 4102
2 | Service |  | Storage tank level
3 | Vessel / tank |  | TK 401, fixed roof
4 | Vessel height |  | 12 |  | m
5 | P&ID number |  | PID 400 01
6 | Hazardous area |  | Zone 1, IIA T3
Process conditions
7 | Liquid |  | Diesel
8 | Density (minimum / maximum) |  | 820 / 860 |  | kg/m³
9 | Dielectric constant |  | 2.1
10 | Operating pressure / temperature |  | Atm / 40 |  | bar g / °C
11 | Design pressure / temperature |  | 0.05 / 80 |  | bar g / °C
12 | Foam, turbulence or coating |  | None
13 | Vapour or dust in the space above |  | Hydrocarbon vapour
Measurement
14 | Measuring principle |  | Non contact radar, 80 GHz
15 | Nozzle size / height |  | DN 80 / roof
16 | Measuring range (from reference) |  | 11.5 |  | m
17 | Range in % of vessel (calculated) |  | 95.8 |  | % of vessel height
18 | Interface measurement |  | No
19 | Accuracy |  | ± 2 |  | mm
20 | Probe / antenna length |  | Lens antenna
21 | Wetted materials |  | PTFE / SS 316L
22 | Stilling well / bypass chamber |  | Not required
Transmitter
23 | Output |  | 4 to 20 mA HART
24 | Ex certification |  | Ex db ia IIC T6 Gb |  | ATEX / IECEx
25 | Enclosure (IP) |  | IP66/67
26 | Display |  | LCD, local
27 | Cable entry |  | M20 x 1.5
Purchase
28 | Manufacturer / model |  | Vendor to specify
29 | Quantity |  | 1 |  | no
Give density for DP and displacer meters, dielectric constant for radar and capacitance, and note foam, turbulence and coating: they decide which principle will work.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date: