## How to Use
HOW TO USE: INSTRUMENT LOOP CHECK SHEET
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Fill the loop details from the loop drawing, I/O list and data sheet. Range and tolerance drive the test calculations.
2. Complete the pre checks before powering the loop. Do not inject signals into a loop with incomplete wiring checks.
3. Disconnect the transmitter (or use it in loop test mode) and inject 4, 8, 12, 16 and 20 mA at the field end; record what the DCS or PLC displays.
4. Simulate each alarm and trip point and confirm the alarm appears on the HMI and in the event log.
5. All parties sign the sheet. Attach it to the loop folder for handover.
What the formulas do
• Injected mA = 4 + 16 × % ÷ 100.
• Expected reading = LRV + span × % ÷ 100.
• Error = (DCS reading − expected) ÷ span × 100; PASS within the loop tolerance.
• Deviation = alarm activation value − set point.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
INSTRUMENT LOOP CHECK SHEET
Company: Your Company Name / Logo |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Loop details
Loop number |  |  |  | Tag number
Service |  |  |  | Instrument type
Range LRV |  |  |  | Range URV
Unit |  |  |  | I/O type
System / controller |  |  |  | Card / channel
Junction box |  |  |  | Field cable / multipair
P&ID number |  |  |  | Loop drawing number
Loop tolerance (± % span) |  |  |  | Test date
Pre checks
No | Check item |  |  |  | Status | Remarks
1 | Instrument installed as per hook up drawing and tag plate fitted
2 | Process connection, impulse lines and manifold leak tested
3 | Cable glanded, terminated and ferruled as per termination schedule
4 | Insulation resistance of loop cable checked (≥ 100 MΩ at 500 V DC, instrument disconnected)
5 | Continuity and polarity checked field to marshalling to I/O card
6 | Shield earthed at one end only (control room side)
7 | IS barrier / isolator type matches the loop drawing (if IS loop)
8 | Instrument range and configuration match the data sheet
Loop test: signal injected at the field, reading checked on DCS / PLC display
Injected (%) | Injected (mA) | Expected reading | DCS / PLC reading | Error (% span) | Result | Remarks
0 | 4
25 | 8
50 | 12
75 | 16
100 | 20
Loop test result
Alarm and trip check
Alarm | Set point | Activated at | Deviation | Shown on HMI and logged? | Remarks
LL
L
H
HH
Contractor |  | Owner / client |  | DCS vendor
Name: |  | Name: |  | Name:
Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date:

## Example
INSTRUMENT LOOP CHECK SHEET
Company: ABC Process Industries Ltd |  |  |  | Doc no: LC PT 1101 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Loop details
Loop number |  | 1101 |  | Tag number |  | PT 1101
Service |  | Steam header pressure |  | Instrument type |  | Pressure transmitter, 2 wire HART
Range LRV |  | 0 |  | Range URV |  | 16
Unit |  | bar g |  | I/O type |  | AI
System / controller |  | DCS controller CP 01 |  | Card / channel |  | AI 03 / CH 05
Junction box |  | JB 11 |  | Field cable / multipair |  | IC 1101 / MP 11 01 pair 5
P&ID number |  | P&ID 100 02 |  | Loop drawing number |  | LD 1101
Loop tolerance (± % span) |  | 0.5 |  | Test date |  | 2026-10-12
Pre checks
No | Check item |  |  |  | Status | Remarks
1 | Instrument installed as per hook up drawing and tag plate fitted |  |  |  | OK
2 | Process connection, impulse lines and manifold leak tested |  |  |  | OK
3 | Cable glanded, terminated and ferruled as per termination schedule |  |  |  | OK
4 | Insulation resistance of loop cable checked (≥ 100 MΩ at 500 V DC, instrument disconnected) |  |  |  | OK
5 | Continuity and polarity checked field to marshalling to I/O card |  |  |  | OK
6 | Shield earthed at one end only (control room side) |  |  |  | OK
7 | IS barrier / isolator type matches the loop drawing (if IS loop) |  |  |  | NA | Non IS loop
8 | Instrument range and configuration match the data sheet |  |  |  | OK
Loop test: signal injected at the field, reading checked on DCS / PLC display
Injected (%) | Injected (mA) | Expected reading | DCS / PLC reading | Error (% span) | Result | Remarks
0 | 4 | 0 | 0 | 0 | PASS
25 | 8 | 4 | 4.01 | 0.0625 | PASS
50 | 12 | 8 | 8.02 | 0.125 | PASS
75 | 16 | 12 | 12.01 | 0.0625 | PASS
100 | 20 | 16 | 16 | 0 | PASS
Loop test result | [5 empty] | PASS
Alarm and trip check
Alarm | Set point | Activated at | Deviation | Shown on HMI and logged? | Remarks
LL
L | 4 | 4 | 0 | Yes
H | 13 | 13 | 0 | Yes
HH | 14.5 | 14.5 | 0 | Yes | Trips boiler feed via SIS (tested separately)
Contractor |  | Owner / client |  | DCS vendor
Name: |  | Name: |  | Name:
Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: