## How to Use
HOW TO USE: PRESSURE SWITCH CALIBRATION REPORT
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter the set point, trip direction and allowed tolerance from the instrument data sheet or alarm and trip list.
2. Connect a continuity tester or multimeter across the contact used in the circuit.
3. Raise the pressure slowly near the set point and record the trip value; lower it until the contact resets and record the reset value. Repeat three times.
4. If the trip is out of tolerance, adjust the range screw and record three as left trials.
5. Check repeatability and deadband, then sign the report.
What the formulas do
• Deadband = ¦trip − reset¦.
• Deviation = trip − set point.
• Result uses as left values when present, otherwise as found; PASS when ¦deviation¦ ≤ tolerance.
• Repeatability = highest trip − lowest trip over the trials.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
PRESSURE SWITCH CALIBRATION REPORT
Company: Your Company Name / Logo |  |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Switch details
Tag number |  |  |  |  | Service
Make and model |  |  |  |  | Serial number
Adjustable range |  |  |  |  | Unit
Set point |  |  |  |  | Trip on
Set point tolerance (±) |  |  |  |  | Contact used
Test equipment
Pressure standard |  |  |  |  | Standard certificate no
Calibration date |  |  |  |  | Work order no
Trip and reset test
Trial | As found trip | As found reset | As found deadband | As found deviation from SP | As left trip | As left reset | As left deadband | As left deviation from SP | Result
1
2
3
As left repeatability (max − min trip)
As left average deadband
Overall result
Performed by |  |  | Checked by |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:

## Example
PRESSURE SWITCH CALIBRATION REPORT
Company: ABC Process Industries Ltd |  |  |  |  | Doc no: CAL PSH 1105 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Switch details
Tag number |  | PSH 1105 |  |  | Service |  | Air receiver high pressure
Make and model |  | Danfoss KPS 35 |  |  | Serial number |  | KPS 60113
Adjustable range |  | 0 to 16 bar |  |  | Unit |  | bar
Set point |  | 8 |  |  | Trip on |  | Rising
Set point tolerance (±) |  | 0.1 |  |  | Contact used |  | NO, opens on trip
Test equipment
Pressure standard |  | Druck DPI 620 |  |  | Standard certificate no |  | NABL/CC 24118
Calibration date |  | 2026-10-12 |  |  | Work order no |  | WO 26 0433
Trip and reset test
Trial | As found trip | As found reset | As found deadband | As found deviation from SP | As left trip | As left reset | As left deadband | As left deviation from SP | Result
1 | 8.25 | 7.62 | 0.63 | 0.25 | 8.03 | 7.55 | 0.48 | 0.03 | PASS
2 | 8.22 | 7.6 | 0.62 | 0.22 | 8.01 | 7.53 | 0.48 | 0.01 | PASS
3 | 8.27 | 7.63 | 0.64 | 0.27 | 8.02 | 7.56 | 0.46 | 0.02 | PASS
As left repeatability (max − min trip) | [7 empty] | 0.02
As left average deadband | [7 empty] | 0.47333
Overall result | [7 empty] | PASS
Performed by |  |  | Checked by |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date: