## How to Use
HOW TO USE: PRESSURE TRANSMITTER CALIBRATION REPORT
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Fill in the instrument details. LRV, URV and tolerance drive every calculation, so enter them first.
2. Record the pressure standard, its certificate number and validity. Never use a standard past its due date.
3. Apply pressure at each test point shown in the Applied pressure column, upscale then downscale, and type the transmitter output in As found output (mA).
4. If any point fails, adjust the transmitter (zero and span or sensor trim) and repeat the test, entering the readings in As left output (mA).
5. Check the overall result, add remarks, then sign and date the report.
What the formulas do
• Applied pressure = LRV + (URV − LRV) × test point % ÷ 100.
• Expected output = 4 + 16 × test point % ÷ 100 mA.
• Error (% of span) = (measured mA − expected mA) ÷ 16 × 100.
• Result is PASS when the absolute error is within the tolerance you entered.
• Overall result uses the as left readings if you adjusted the transmitter, otherwise the as found readings.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
PRESSURE TRANSMITTER CALIBRATION REPORT
Company: Your Company Name / Logo |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Instrument details
Tag number |  |  |  | Service
Make and model |  |  |  | Serial number
Calibrated range LRV |  |  |  | Calibrated range URV
Engineering unit |  |  |  | Output
Tolerance (± % of span) |  |  |  | Location
Test equipment and conditions
Pressure standard |  |  |  | Standard certificate no
Standard valid until |  |  |  | Calibration date
Ambient temperature (°C) |  |  |  | Work order no
Calibration results (5 point, upscale and downscale)
Test point (% of span) | Applied pressure | Expected output (mA) | As found output (mA) | As found error (% span) | As found result | As left output (mA) | As left error (% span) | As left result
0 |  | 4
25 |  | 8
50 |  | 12
75 |  | 16
100 |  | 20
75 |  | 16
50 |  | 12
25 |  | 8
0 |  | 4
Maximum as found error (% span)
Maximum as left error (% span)
Overall result (as left if adjusted, else as found)
Remarks: As found readings exceeded tolerance above 50 % of span. Zero and span trimmed with HART communicator; as left within ± 0.25 % of span.
Performed by |  |  | Checked by |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:

## Example
PRESSURE TRANSMITTER CALIBRATION REPORT
Company: ABC Process Industries Ltd |  |  |  | Doc no: CAL PT 1101 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Instrument details
Tag number |  | PT 1101 |  | Service |  | Steam header pressure
Make and model |  | Rosemount 3051TG |  | Serial number |  | 3051 0098812
Calibrated range LRV |  | 0 |  | Calibrated range URV |  | 16
Engineering unit |  | bar g |  | Output |  | 4 to 20 mA HART
Tolerance (± % of span) |  | 0.25 |  | Location |  | Boiler house, EL +6.0 m
Test equipment and conditions
Pressure standard |  | Fluke 754 + 700G07 |  | Standard certificate no |  | NABL/CC 24117
Standard valid until |  | 2027-03-31 |  | Calibration date |  | 2026-10-12
Ambient temperature (°C) |  | 29 |  | Work order no |  | WO 26 0412
Calibration results (5 point, upscale and downscale)
Test point (% of span) | Applied pressure | Expected output (mA) | As found output (mA) | As found error (% span) | As found result | As left output (mA) | As left error (% span) | As left result
0 | 0 | 4 | 4.012 | 0.075 | PASS | 4.001 | 0.00625 | PASS
25 | 4 | 8 | 8.031 | 0.19375 | PASS | 8.003 | 0.01875 | PASS
50 | 8 | 12 | 12.058 | 0.3625 | FAIL | 12.002 | 0.0125 | PASS
75 | 12 | 16 | 16.071 | 0.44375 | FAIL | 15.998 | -0.0125 | PASS
100 | 16 | 20 | 20.079 | 0.49375 | FAIL | 20.002 | 0.0125 | PASS
75 | 12 | 16 | 16.068 | 0.425 | FAIL | 16.001 | 0.00625 | PASS
50 | 8 | 12 | 12.052 | 0.325 | FAIL | 12.004 | 0.025 | PASS
25 | 4 | 8 | 8.027 | 0.16875 | PASS | 8.002 | 0.0125 | PASS
0 | 0 | 4 | 4.01 | 0.0625 | PASS | 3.999 | -0.00625 | PASS
Maximum as found error (% span) | [6 empty] | 0.49375
Maximum as left error (% span) | [6 empty] | 0.025
Overall result (as left if adjusted, else as found) | [6 empty] | PASS
Remarks: As found readings exceeded tolerance above 50 % of span. Zero and span trimmed with HART communicator; as left within ± 0.25 % of span.
Performed by |  |  | Checked by |  |  | Approved by
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date: