## How to Use
HOW TO USE: SITE ACCEPTANCE TEST (SAT) CHECKLIST
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Confirm the pre requisites first: SAT should not start until installation and cold loop checks are complete.
2. Work through the checklist with the client and operations representatives.
3. Record PASS, FAIL or NA and remarks. Raise punch items for every FAIL.
4. SAT status turns PASS only when every row is tested and none has failed.
5. Sign off and include the checklist in the handover dossier.
What the formulas do
• Counts of PASS, FAIL and untested rows.
• SAT status: FAIL if any failure, CHECK while rows remain untested, else PASS.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
SITE ACCEPTANCE TEST (SAT) CHECKLIST
Company: Your Company Name / Logo |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Project
Project |  |  |  | Client
System |  |  |  | Site
SAT start date |  |  |  | SAT procedure
Test checklist
No | Section | Check item |  |  | Acceptance criteria |  | Result | Remarks
1 | Pre requisites | FAT punch items closed or accepted |  |  | No open category A items
2 | Pre requisites | Panel installed, levelled, earthed and glanded |  |  | As per layout and earthing drawings
3 | Pre requisites | Field installation checklists and cold loop checks complete |  |  | Signed records available
4 | Power | UPS and power distribution energised, voltages checked |  |  | Within ± 5 % of nominal
5 | Power | Earth resistance of instrument earth pit |  |  | As specified, typically ≤ 1 Ω
6 | System | System healthy after power up, no diagnostic alarms |  |  | All cards and nodes healthy
7 | System | Time synchronisation across controllers and HMIs |  |  | All nodes show the same time
8 | Loops | Hot loop checks of all field instruments |  |  | Loop check sheets signed
9 | Loops | Control valves stroked from HMI |  |  | Position matches demand
10 | Loops | Motor start / stop and feedback from MCC |  |  | Correct status and fault indication
11 | Communication | Links to MCC, VFDs, analysers and package PLCs |  |  | Live data verified
12 | Communication | Link to plant historian / MES |  |  | Tags updating
13 | Logic | Interlocks tested with real field devices |  |  | As per cause and effect
14 | Logic | Start up and shutdown sequences dry run |  |  | As per operating philosophy
15 | HMI | Alarm set points and priorities as per alarm list |  |  | Verified
16 | HMI | Reports, trends and printers working |  |  | Verified
17 | Final | Operator training completed |  |  | Attendance record
18 | Final | As built drawings, backups and manuals handed over |  |  | Transmittal signed
PASS | [6 empty] | 0
FAIL | [6 empty] | 0
Not yet tested | [6 empty] | 18
SAT status
Contractor |  |  | Client |  |  | Operations
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date:

## Example
SITE ACCEPTANCE TEST (SAT) CHECKLIST
Company: ABC Process Industries Ltd |  |  |  | Doc no: SAT CP 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Project
Project |  | Boiler 3 control system upgrade |  | Client |  | ABC Process Industries Ltd
System |  | PLC panel CP 03, HMI 1, HMI 2 |  | Site |  | Utilities block, Pune plant
SAT start date |  | 2026-11-02 |  | SAT procedure |  | SAT PROC 03 Rev 0
Test checklist
No | Section | Check item |  |  | Acceptance criteria |  | Result | Remarks
1 | Pre requisites | FAT punch items closed or accepted |  |  | No open category A items |  | PASS
2 | Pre requisites | Panel installed, levelled, earthed and glanded |  |  | As per layout and earthing drawings |  | PASS
3 | Pre requisites | Field installation checklists and cold loop checks complete |  |  | Signed records available |  | PASS
4 | Power | UPS and power distribution energised, voltages checked |  |  | Within ± 5 % of nominal |  | PASS
5 | Power | Earth resistance of instrument earth pit |  |  | As specified, typically ≤ 1 Ω |  | PASS
6 | System | System healthy after power up, no diagnostic alarms |  |  | All cards and nodes healthy |  | PASS
7 | System | Time synchronisation across controllers and HMIs |  |  | All nodes show the same time |  | PASS
8 | Loops | Hot loop checks of all field instruments |  |  | Loop check sheets signed |  | PASS
9 | Loops | Control valves stroked from HMI |  |  | Position matches demand |  | PASS
10 | Loops | Motor start / stop and feedback from MCC |  |  | Correct status and fault indication |  | PASS
11 | Communication | Links to MCC, VFDs, analysers and package PLCs |  |  | Live data verified |  | PASS
12 | Communication | Link to plant historian / MES |  |  | Tags updating |  | FAIL | Historian OPC tags not updating; firewall rule pending
13 | Logic | Interlocks tested with real field devices |  |  | As per cause and effect |  | PASS
14 | Logic | Start up and shutdown sequences dry run |  |  | As per operating philosophy |  | PASS
15 | HMI | Alarm set points and priorities as per alarm list |  |  | Verified |  | PASS
16 | HMI | Reports, trends and printers working |  |  | Verified |  | PASS
17 | Final | Operator training completed |  |  | Attendance record
18 | Final | As built drawings, backups and manuals handed over |  |  | Transmittal signed
PASS | [6 empty] | 15
FAIL | [6 empty] | 1
Not yet tested | [6 empty] | 2
SAT status | [6 empty] | FAIL
Contractor |  |  | Client |  |  | Operations
Name: |  |  | Name: |  |  | Name:
Signature: |  |  | Signature: |  |  | Signature:
Date: |  |  | Date: |  |  | Date: