## How to Use
HOW TO USE: SIF PROOF TEST RECORD
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Fill in the SIF details and the proof test interval from the safety requirements specification.
2. Record each measured trip point with its required value and tolerance.
3. Measure the response time of each final element with a stopwatch or the DCS sequence of events.
4. Mark each test step PASS, FAIL or NA, and remark on anything abnormal.
5. A dangerous failure found during the test must be reported, repaired and the SIF retested before being returned to service.
What the formulas do
• Trip point result = PASS if ¦as found − required¦ ≤ tolerance.
• Response time result = PASS if measured ≤ required maximum.
• Select the overall result FAIL if any item or step failed.
• Next test due = test date + proof test interval.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
SIF PROOF TEST RECORD
Company: Your Company Name / Logo |  |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Safety function
SIF number |  |  |  | Description
SIL |  |  |  | Architecture
Proof test interval (months) |  |  |  | Test date
Next test due |  |  |  | Test procedure
Measured values
Item |  | Required | Tolerance (±) | As found | Result | Unit
Measured items failed | [5 empty] | 0
Response time
Final element |  | Required max (s) | Measured (s) | Result | Remarks
Response times failed | [5 empty] | 0
Test steps
No | Check item |  |  |  | Status | Remarks
1 | Permit and bypass authorised; operations informed
2 | Initiator isolated and test equipment connected
3 | Trip simulated at the initiator (or process taken to trip)
4 | Logic solver trip and alarm received in DCS
5 | Final element moved to safe position
6 | Valve stroke observed full travel and limit switch feedback received
7 | Tight shut off checked (where required)
8 | Reset and restore to normal; bypass removed
9 | Initiator returned to service and reading compared with other sensors
Steps failed | [5 empty] | 0
Overall
Proof test result |  |  |  | Dangerous failures found
Tested by |  | Witnessed by (operations) |  | Approved by
Name: |  | Name: |  | Name:
Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date:

## Example
SIF PROOF TEST RECORD
Company: ABC Process Industries Ltd |  |  |  | Doc no: PTR SIF 001 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Safety function
SIF number |  | SIF 101 |  | Description |  | High high steam pressure: trip burner
SIL |  | SIL 2 |  | Architecture |  | Sensors 2oo3, valves 1oo2
Proof test interval (months) |  | 12 |  | Test date |  | 2026-10-14
Next test due |  | 2027-10-14 |  | Test procedure |  | PT PROC 101 rev B
Measured values
Item |  | Required | Tolerance (±) | As found | Result | Unit
PT 1101 A trip point |  | 14.5 | 0.15 | 14.56 | PASS | bar g
PT 1101 B trip point |  | 14.5 | 0.15 | 14.41 | PASS | bar g
PT 1101 C trip point |  | 14.5 | 0.15 | 14.62 | PASS | bar g
Measured items failed | [5 empty] | 0
Response time
Final element |  | Required max (s) | Measured (s) | Result | Remarks
XV 1101 fuel gas SDV |  | 3 | 2.1 | PASS | Full stroke, limit switch OK
XV 1102 fuel gas SDV |  | 3 | 2.4 | PASS
Response times failed | [5 empty] | 0
Test steps
No | Check item |  |  |  | Status | Remarks
1 | Permit and bypass authorised; operations informed |  |  |  | PASS
2 | Initiator isolated and test equipment connected |  |  |  | PASS
3 | Trip simulated at the initiator (or process taken to trip) |  |  |  | PASS | Simulated with hand pump at transmitter
4 | Logic solver trip and alarm received in DCS |  |  |  | PASS
5 | Final element moved to safe position |  |  |  | PASS
6 | Valve stroke observed full travel and limit switch feedback received |  |  |  | PASS
7 | Tight shut off checked (where required) |  |  |  | NA | Not required for this SIF
8 | Reset and restore to normal; bypass removed |  |  |  | PASS
9 | Initiator returned to service and reading compared with other sensors |  |  |  | PASS
Steps failed | [5 empty] | 0
Overall
Proof test result |  | PASS |  | Dangerous failures found |  | None
Tested by |  | Witnessed by (operations) |  | Approved by
Name: |  | Name: |  | Name:
Signature: |  | Signature: |  | Signature:
Date: |  | Date: |  | Date: