## How to Use
HOW TO USE: SOLENOID VALVE DATA SHEET
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Define function and normal state.
2. Give supply pressure range and medium.
3. Choose valve type and size so the actuator vents within the required time.
4. Specify coil voltage, power and Ex marking.
5. Add SIL and manual override needs.
What the formulas do
• No formulas: specification document laid out in sections like an ISA 20 style data sheet.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
SOLENOID VALVE DATA SHEET
Company: Your Company Name / Logo |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  |  | Revision
Date |  |  | Requisition no
Specification
No | Parameter |  | Value | Unit / notes
General
1 | Tag number
2 | Function
3 | Associated valve
4 | Hazardous area
5 | SIL requirement
Service
6 | Medium
7 | Supply pressure (min / max)
8 | Ambient temperature
Valve
9 | Type (3/2, 5/2, direct or pilot)
10 | Normal state (energised / de energised)
11 | Port size / Cv
12 | Body material
13 | Seal material
14 | Manual override
Coil
15 | Voltage
16 | Power
17 | Ex certification
18 | Coil class / duty
19 | Cable entry
Purchase
20 | Manufacturer / model
21 | Quantity
For shutdown duty, de energise to trip with a 3/2 valve of enough Cv to meet the stroke time. Check the coil power against the safety system output rating.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date:

## Example
SOLENOID VALVE DATA SHEET
Company: ABC Process Industries Ltd |  |  | Doc no: DS XY 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  | Boiler 3 upgrade | Revision | A
Date |  | 2026-10-24 | Requisition no | REQ INST 037
Specification
No | Parameter |  | Value |  | Unit / notes
General
1 | Tag number |  | XY 4101
2 | Function |  | ESD valve actuator vent
3 | Associated valve |  | XV 4101
4 | Hazardous area |  | Zone 2, IIB T3
5 | SIL requirement |  | SIL 2 capable
Service
6 | Medium |  | Instrument air
7 | Supply pressure (min / max) |  | 4.5 / 7 |  | bar g
8 | Ambient temperature |  | −5 to 50 |  | °C
Valve
9 | Type (3/2, 5/2, direct or pilot) |  | 3/2, direct acting
10 | Normal state (energised / de energised) |  | Energised in normal operation |  | De energise to trip
11 | Port size / Cv |  | 1/4" / 0.6
12 | Body material |  | SS 316
13 | Seal material |  | FKM
14 | Manual override |  | Locking, latched
Coil
15 | Voltage |  | 24 V DC
16 | Power |  | < 2 |  | W
17 | Ex certification |  | Ex db IIC T4 Gb
18 | Coil class / duty |  | Class F, 100 % ED
19 | Cable entry |  | M20 x 1.5
Purchase
20 | Manufacturer / model |  | Vendor to specify
21 | Quantity |  | 1 |  | no
For shutdown duty, de energise to trip with a 3/2 valve of enough Cv to meet the stroke time. Check the coil power against the safety system output rating.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date: