## How to Use
HOW TO USE: TEMPERATURE ELEMENT AND TRANSMITTER DATA SHEET
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Enter process conditions, including fluid velocity, which is needed for the thermowell calculation.
2. Choose the element type, tolerance class and number of wires (4 wire for best RTD accuracy).
3. Specify thermowell type, connection, material and dimensions; request the wake frequency calculation.
4. Specify the transmitter range, output and burnout direction so a sensor failure drives the loop safe.
5. Issue with the requisition for vendor completion.
What the formulas do
• No formulas: specification document.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
TEMPERATURE ELEMENT AND TRANSMITTER DATA SHEET
Company: Your Company Name / Logo |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  |  | Revision
Date |  |  | Requisition no
Specification
No | Parameter |  | Value | Unit / notes
General
1 | Tag number
2 | Service
3 | Line or equipment
4 | P&ID number
5 | Hazardous area
Process conditions
6 | Fluid
7 | Operating temperature (normal / maximum)
8 | Design pressure / temperature
9 | Fluid velocity
10 | Pipe size (for immersion length)
Element
11 | Element type
12 | Tolerance class
13 | Number of elements / wires
14 | Sheath diameter / material
15 | Insertion length (U)
Thermowell
16 | Thermowell type
17 | Process connection
18 | Material
19 | Bore / tip diameter
20 | Wake frequency calculation (ASME PTC 19.3 TW)
Transmitter
21 | Mounting
22 | Input / range
23 | Output
24 | Sensor fault (burnout) direction
25 | Ex certification
26 | Enclosure (IP)
Purchase
27 | Manufacturer / model
28 | Quantity
Ask the vendor for a thermowell wake frequency and stress calculation to ASME PTC 19.3 TW at maximum velocity, especially for gas and steam lines and long wells.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date:

## Example
TEMPERATURE ELEMENT AND TRANSMITTER DATA SHEET
Company: ABC Process Industries Ltd |  |  | Doc no: DS TT 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  | Reactor 2 revamp | Revision | A
Date |  | 2026-10-14 | Requisition no | REQ INST 023
Specification
No | Parameter |  | Value |  | Unit / notes
General
1 | Tag number |  | TT 2101
2 | Service |  | Reactor jacket outlet
3 | Line or equipment |  | 4" / Sch 40 line
4 | P&ID number |  | PID 200 03
5 | Hazardous area |  | Zone 2, IIB T3
Process conditions
6 | Fluid |  | Hot water
7 | Operating temperature (normal / maximum) |  | 120 / 160 |  | °C
8 | Design pressure / temperature |  | 10 / 180 |  | bar g / °C
9 | Fluid velocity |  | 2.5 |  | m/s
10 | Pipe size (for immersion length) |  | 4" Sch 40
Element
11 | Element type |  | Pt100, 4 wire |  | IEC 60751
12 | Tolerance class |  | Class A
13 | Number of elements / wires |  | 1 / 4
14 | Sheath diameter / material |  | 6 mm / SS 316
15 | Insertion length (U) |  | 150 |  | mm
Thermowell
16 | Thermowell type |  | Tapered, bar stock
17 | Process connection |  | 1" ASME 300 RF flange
18 | Material |  | SS 316
19 | Bore / tip diameter |  | 6.6 / 16 |  | mm
20 | Wake frequency calculation (ASME PTC 19.3 TW) |  | Required |  | by vendor
Transmitter
21 | Mounting |  | Head mounted
22 | Input / range |  | Pt100, 0 to 200 °C
23 | Output |  | 4 to 20 mA HART
24 | Sensor fault (burnout) direction |  | Upscale (≥ 21 mA) |  | NAMUR NE43
25 | Ex certification |  | Ex nA IIC T4 Gc
26 | Enclosure (IP) |  | IP66
Purchase
27 | Manufacturer / model |  | Vendor to specify
28 | Quantity |  | 1 |  | set
Ask the vendor for a thermowell wake frequency and stress calculation to ASME PTC 19.3 TW at maximum velocity, especially for gas and steam lines and long wells.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date: