## How to Use
HOW TO USE: THERMOWELL DATA SHEET
Colour legend
Yellow cells: type your data here.
Grey cells: formulas. They calculate automatically; do not overwrite them.
Steps
1. Fill in process conditions, especially maximum velocity and density.
2. Choose profile, connection and insertion length.
3. Specify bore to suit the sensor diameter.
4. Request the wake frequency calculation and material certificates.
5. Issue with the requisition.
What the formulas do
• No formulas: specification document laid out in sections like an ISA 20 style data sheet.
Sheets: "Template" is blank and ready to use. "Example" shows a completed form so you can see the expected format.
More free templates, calculators and tools: https://instrumentationblog.in/downloads/templates/

## Template
THERMOWELL DATA SHEET
Company: Your Company Name / Logo |  |  | Doc no: Rev:
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  |  | Revision
Date |  |  | Requisition no
Specification
No | Parameter |  | Value | Unit / notes
General
1 | Tag number
2 | Sensor tag / type
3 | Line number / size
4 | P&ID number
Process
5 | Fluid
6 | Operating pressure / temperature
7 | Design pressure / temperature
8 | Maximum velocity
9 | Density / viscosity
Thermowell
10 | Construction (bar stock, fabricated)
11 | Profile (straight, tapered, stepped)
12 | Process connection
13 | Insertion length U
14 | Root and tip diameter
15 | Bore diameter
16 | Material
17 | Wake frequency calculation (ASME PTC 19.3 TW)
Tests
18 | Hydrostatic test
19 | Material certificate
20 | Radiography / dye penetrant
Purchase
21 | Manufacturer / model
22 | Quantity
Always give maximum velocity and density: they drive the vortex shedding check. Ask for the PTC 19.3 TW calculation with the offer.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date:

## Example
THERMOWELL DATA SHEET
Company: ABC Process Industries Ltd |  |  | Doc no: DS TW 01 Rev: 0
Yellow cells: enter data. Grey cells: calculated automatically. Free template from instrumentationblog.in
Document
Project |  | Boiler 3 upgrade | Revision | A
Date |  | 2026-10-24 | Requisition no | REQ INST 035
Specification
No | Parameter |  | Value |  | Unit / notes
General
1 | Tag number |  | TW 2205
2 | Sensor tag / type |  | TE 2205, Pt100
3 | Line number / size |  | 6" Sch 40
4 | P&ID number |  | PID 200 05
Process
5 | Fluid |  | Steam
6 | Operating pressure / temperature |  | 16 / 250 |  | bar g / °C
7 | Design pressure / temperature |  | 20 / 300 |  | bar g / °C
8 | Maximum velocity |  | 30 |  | m/s
9 | Density / viscosity |  | 7.1 / 0.02 |  | kg/m³ / cP
Thermowell
10 | Construction (bar stock, fabricated) |  | Bar stock
11 | Profile (straight, tapered, stepped) |  | Tapered
12 | Process connection |  | 1 1/2" ASME 300 RF
13 | Insertion length U |  | 200 |  | mm
14 | Root and tip diameter |  | 27 / 19 |  | mm
15 | Bore diameter |  | 6.6 |  | mm
16 | Material |  | SS 316
17 | Wake frequency calculation (ASME PTC 19.3 TW) |  | Required, passed |  | Vendor to submit
Tests
18 | Hydrostatic test |  | Yes |  | Vendor standard
19 | Material certificate |  | EN 10204 3.1
20 | Radiography / dye penetrant |  | Dye penetrant on weld
Purchase
21 | Manufacturer / model |  | Vendor to specify
22 | Quantity |  | 1 |  | no
Always give maximum velocity and density: they drive the vortex shedding check. Ask for the PTC 19.3 TW calculation with the offer.
Prepared by |  | Checked by | Approved by
Name: |  | Name: | Name:
Signature: |  | Signature: | Signature:
Date: |  | Date: | Date: